## about
Table | grid_events
Description | SOLAR & WIND OUTAGE EVENTS. Every grid disturbance / incident in Grid-India's monthly reports, with start, end, generation lost and narrative; involves_re marks events that took solar, wind or other renewable plants offline (usually by loss of the evacuation line, not a fault inside the plant).
Period | 2025-10-13 to 2026-10-12
Rows | 521
Sources | Central Electricity Authority (npp.gov.in, gen-re.cea.gov.in); Grid Controller of India (grid-india.in). Every value traces to a file in source_files via source_file_id.
Rebuild | python -m observatory refresh (see README)
Column | Meaning
event_id | Identifier of the event in this release
month | Month of the Grid-India report (YYYY-MM)
seq | Position of the event in that month's report
category | Grid-India event category: GD-1..GD-5 (grid disturbance), GI-1/GI-2 (grid incident), NEAR MISS
state | State / UT name (normalised)
state_code | Two-letter state / UT code (reference/states.csv)
region | Grid region (Northern, Western, Southern, Eastern, North-Eastern)
start | Event start date-time
end | Event end (restoration) date-time
duration_h | Hours from outage start to reported return (observed events only)
generation_loss_mw | Generation lost in the event (MW)
load_loss_mw | Load lost in the event (MW)
involves_solar | Narrative mentions solar generation
involves_wind | Narrative mentions wind generation
involves_hybrid | Narrative mentions hybrid (solar + wind) plants
involves_bess | Narrative mentions battery storage (BESS)
involves_re | Event involves solar, wind or other renewable plants
summary | The report's sentence on generation loss (or the start of the narrative)
narrative | Event description as published (first 1,500 characters)
source_file_id | Key into source_files: source/report/date

## data
event_id | month | seq | category | state | state_code | region | start | end | duration_h | generation_loss_mw | load_loss_mw | involves_solar | involves_wind | involves_hybrid | involves_bess | involves_re | summary | narrative | source_file_id
G00001 | 2025-10 | 20 | GD-1 | WR |  |  | 2025-10-13T23:26 | 2025-10-14T13:22 | 13.93 | 153.4 |  | FALSE | FALSE | FALSE | FALSE | FALSE | This resulted in a generation loss of approximately 30 MW due to loss of the evacuation path. | 7 GD-1 WR 13-10-2025 23:26 14-10-2025 13:22 13:56 153.4 - 0.24% - 65253 57141 Complete outage of 220 kV Tuljapur S/S: At 23:36 hrs/13-10-2025, the 400 kV Tuljapur-Konhali line tripped due to 87L protection relay general pickup operated at Tuljapur. Line is holding from Konhali. This resulted in a generation loss of approximately 30 MW due to loss of the evacuation path. 1 400kV Tuljapur-Konhali line-1 2 200 MVA 400/33kV Tuljapur ICT-1 Elements Tripped Details of Grid Events during the Month of October 2025 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of October 2025 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in | grid_india_gd/grid_events/2025-10-01
G00002 | 2025-10 | 8 | GD-1 | Uttar Pradesh | UP | Northern | 2025-10-15T11:58 | 2025-10-15T12:08 | 0.17 | 0 | 230 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GD-1 Uttar Pradesh 15-10-2025 11:58 15-10-2025 12:08 00:10 0 230 0.000 0.400 54865 57521 i) 220/132kV Nehtaur(UP) S/s has main and transfer bus scheme at both 220kV and 132kV level. During antecedent condition, 220 KV Amroha- Morabadbad Ckt had already tripped (at 10:30 Hrs) , hence no supply feed | 8 GD-1 Uttar Pradesh 15-10-2025 11:58 15-10-2025 12:08 00:10 0 230 0.000 0.400 54865 57521 i) 220/132kV Nehtaur(UP) S/s has main and transfer bus scheme at both 220kV and 132kV level. During antecedent condition, 220 KV Amroha- Morabadbad Ckt had already tripped (at 10:30 Hrs) , hence no supply feed was present from 220 KV Amroha. ii) As reported, at 11:58 hrs, Y-N fault appeared in 220 KV Meerut(PG) -Nehtaur(UP) (UP) Ckt and line auto-reclosed successfully. But Y-N phase to earth fault again appeared within reclaim time and finally the line tripped. As per DR at Nehtaur(UP) , fault current was 1.8kA and fault distance was 22.7km (31.0 %) from Nehtaur(UP) end; zone-1 distance protection operated at Nehtaur(UP) end. iii) As no supply feed was present from 220 KV Amroha, supply fail occurred at 220/132kV Nehtaur(UP) . 220 KV Amroha-Nehtaur (UP) Ckt was hand tripped for safety purpose and complete blackout occurred at 220/132kV Nehtaur(UP) S/s. iv) As per PMU at Meerut(PG) , three consecutive Y-N, R-N and Y-N Phase to earth faults were observed with fault clearing time of 120 ms each. v) As per SCADA, change in demand of approx 230 MW was observed in UP control area. 1) 220 KV Meerut(PG)-Nehtaur(UP) (UP) Ckt 2) 220 KV Amroha-Nehtaur (UP) Ckt | grid_india_gd/grid_events/2025-10-01
G00003 | 2025-10 | 7 | GD-1 | Rajasthan | RJ | Northern | 2025-10-15T12:11 | 2025-10-15T12:48 | 0.62 | 1855 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi) As per PMU at CSPJP(IP) and Saurya Urja(IP) , solar generation loss of approx 246 MW and 273 MW were observed at CSPJP(IP) and Saurya Urja(IP) respectively. | 7 GD-1 Rajasthan 15-10-2025 12:11 15-10-2025 12:48 00:37 1855 0 3.378 0.000 54915 56880 i) Generation of 220kV Clean Solar Power Jodhpur (CSPJP) (IP) and 220kV Saurya Urja(IP) station evacuates respectively through 220 KV Bhadla(PG) -CS_Jodhpur SL_BHD_PG (CSPJP) (Cleansolar_Jodhpur) Ckt and 220 KV Bhadla(PG) -Saurya Urja Solar(SU) (Saurya Urja) Ckt-1 & 2. ii) During antecedent condition, 220kV Clean Solar Power Jodhpur (CSPJP) (IP) and 220kV Saurya Urja(IP) station were generating approx 246 MW and 463 MW (Ckt-1 carrying 190 MW and Ckt-2 carrying 273 MW) respectively (as per PMU) . iii) As reported, at 12:11hrs, 220 KV Bhadla(PG) -CS_Jodhpur SL_BHD_PG (CSPJP) (Cleansolar_Jodhpur) Ckt tripped on Y-B Phase to phase fault due to snapping of jumper (exact location yet to be shared) . As per DR at Bhadla(PG) end, line differential protection operated in Main-2 relay with fault current of Iy=~28.22kA, Ib=~28.30kA from Bhadla(PG) end; fault sensed in zone-1 in main-1 relay; fault clearing time was ~56 ms. iv) During the same time, 220 KV Bhadla(PG) -Saurya Urja Solar(SU) (Saurya Urja) Ckt-2 also tripped from Saurya Urja(IP) end only (exact reason and nature of protection operated yet to be shared) . v) As per PMU at Bhadla(PG) , Y-B Phase to phase fault was observed with fault clearing time of ~120ms. Voltage dipped upto 0.775 pu. Frequency decreased from 50.023 Hz to 49.833 Hz (max change in frequency=~0.19 Hz) . vi) As per PMU at CSPJP(IP) and Saurya Urja(IP) , solar generation lo | grid_india_gd/grid_events/2025-10-01
G00004 | 2025-10 | 6 | GD-1 | Rajasthan | RJ | Northern | 2025-10-15T13:15 | 2025-10-15T15:17 | 2.03 | 282 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | v) As per PMU, solar generation loss of approx 282 MW was observed at AHEJ2L(IP) . | 6 GD-1 Rajasthan 15-10-2025 13:15 15-10-2025 15:17 02:02 282 0 0.525 0.000 53668 54101 i) Generation of 220kV AHEJ2L(IP) station evacuates through 220 KV Fatehgarh_II(PG) -AHEJ2L PSS HB_FGRAH_PG (AHEJ2L) (AHEJ2L) Ckt which is further connected to 220/33 kV 150 MVA ICT 1 & 2 at AHEJ2L(IP) . ii) During antecedent condition, 220kV AHEJ2L(IP) station was generating approx 282 MW (as per PMU) . iii) As reported, at 13:15hrs, 220 KV Fatehgarh_II(PG) -AHEJ2L PSS HB_FGRAH_PG (AHEJ2L) (AHEJ2L) Ckt tripped on R-Y phase to phase fault (exact nature, location and reason of fault yet to be shared) which led to complete blackout out of 220kV AHEJ2L(IP) S/s. iv) As per PMU at Fatehgarh2(PG) , R-Y phase to phase fault was observed with fault clearing time of 120ms. Voltage dipped upto 0.788 pu during fault. v) As per PMU, solar generation loss of approx 282 MW was observed at AHEJ2L(IP) . 1) 220 KV Fatehgarh_II(PG)-AHEJ2L PSS HB_FGRAH_PG (AHEJ2L) (AHEJ2L) Ckt | grid_india_gd/grid_events/2025-10-01
G00005 | 2025-10 | 21 | GD-1 | WR |  |  | 2025-10-16T21:39 | 2025-10-17T01:12 | 3.55 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | No Generation loss occurred at Avikiran Baranda due to the event. | 8 GD-1 WR 16-10-2025 21:39 17-10-2025 01:12 03:33 - - - - 68278 59632 Complete outage of 220 kV Baranda S/S: At 21:39 hrs/16-10-2025, 220KV Baranda-Bhuj line tripped in B Phase to Earth fault. Foreign material string was found on B phase at tower no. AP -06 during patrolling. No Generation loss occurred at Avikiran Baranda due to the event. 1. 220 kV Bhuj-Baranda-1 | grid_india_gd/grid_events/2025-10-01
G00006 | 2025-10 | 9 | GI-1 | Uttarakhand | UK | Northern | 2025-10-18T12:09 | 2025-10-18T13:09 | 1 | 0 | 65 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Khodri(UK)-Majri(HP) (UK) Ckt-2 2) 220 KV Khodri - Chhibro (UK) Ckt-2 3) 220 KV Saharanpur(UP)-Khodri(UK) (UP) Ckt 4) 220/132 kV 100 MVA ICT at Khodri(UK) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of October 2025 in N | 9 GI-1 Uttarakhand 18-10-2025 12:09 18-10-2025 13:09 01:00 0 65 0.000 0.111 56489 58823 i) 220KV Khodri(UK) generating station have 4 generating units each of 30MW and have double main bus scheme. ii) During antecedent condition, only 30 MW Unit-3 at Khodri(UK) was in running condition and was generating approx 22 MW (as per SCADA) . iii) As reported, at 12:09 hrs, during the synchronisation of 30 MW Unit-2 at Khodri(UK) , restricted earth fault protection of UAT operated (exact reason, location and nature of fault yet to be shared) . However, due to delayed opening of CB of Unit-2, LBB protection operated. iv) LBB protection issued tripping commands to 220 KV Khodri(UK) -Majri(HP) (UK) Ckt-2, 220 KV Khodri - Chhibro (UK) Ckt-2, 220 KV Saharanpur(UP) -Khodri(UK) (UP) Ckt and 220/132 kV 100 MVA ICT at Khodri(UK) to isolate the fault. v) As per PMU at Saharanpur(PG) , three phase to earth fault with fault clearing time of 280 ms was observed. vi) As per SCADA, change in demand of approx 65 MW was observed in Uttarakhand control area. 1) 220 KV Khodri(UK)-Majri(HP) (UK) Ckt-2 2) 220 KV Khodri - Chhibro (UK) Ckt-2 3) 220 KV Saharanpur(UP)-Khodri(UK) (UP) Ckt 4) 220/132 kV 100 MVA ICT at Khodri(UK) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of October 2025 in Northern Region Elements Tripped Sl No. Affected Area | grid_india_gd/grid_events/2025-10-01
G00007 | 2025-10 | 22 | GI-2 | WR |  |  | 2025-10-19T00:26 | 2025-10-19T02:44 | 2.3 | 15 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 15 MW occurred at 220 kV Dedhiya WPP due to Bus coupler tripping. | 9 GI-2 WR 19-10-2025 00:26 19-10-2025 02:44 02:18 15 - 0.02% - 63968 56547 Partial outage of 400 kV Khavda PS2 S/S: At 26:57 Hrs/19.10.2025, 765/400 kV Khavda PS2 ICT 4 tripped on Differential (B-E fault) protection operation. • At 00:27:01 Hrs, 220 kV Dedhiya Bus coupler tripped on Over Voltage protection operation. Due to Bus coupler tripping, 220/33 kV Dedhiya ICT 2 along with 220 kV Dedhiya Bus 1 became dead. Tripping of 220 kV Dedhiya Bus coupler on Over Voltage protection operation is undesirable and settings needs to be reviewed. • At 00:27:02 Hrs (after 5 seconds of 765/400 kV Khavda PS2 ICT 4 tripping), 765 kV Bhuj- Khavda PS1 ckt 2 & 765 kV Lakadiya- Ahmedabad 1 (anti-theft charged from Lakadiya end upto 56 km) tripped on Over Voltage Stage I protection operation at Khavda PS1 & Lakadiya ends respectively. • As seen from PMU plot, Voltage of 765 kV Bhuj- Khavda PS1 ckt 2 at Khavda PS1 end increased from 782 kV to 828 kV (108%) and resulted in Over Voltage protection operation and receipt of DT at Bhuj end. Generation loss of 15 MW occurred at 220 kV Dedhiya WPP due to Bus coupler tripping. 1 765/400 kV Khavda PS2 ICT 4 2 765 kV Bhuj- Khavda PS1 ckt 2 3 765 kV Lakadiya- Ahmedabad 1 4 220 kV Dehdiya Bus coupler 5 220 kV Dehdiya Bus 1 6 220/33 kV Dedhiya ICT 2 | grid_india_gd/grid_events/2025-10-01
G00008 | 2025-10 | 23 | GD-1 | WR |  |  | 2025-10-20T21:51 | 2025-10-21T04:15 | 6.4 | 1.2 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 WR 20-10-2025 21:51 21-10-2025 04:15 06:24 1.2 - 0.00% - 54407 47271 Complete outage of 220 kV Gadsisa S/S: At 21:51 Hrs/20-10-2025, 220kV Bhuj–Gadhsisa line tripped due to B phase to ground fault (CT jumper opened at Bhuj end), fault current- 23.8KA, 1.01 km from Bhuj end. 1 220kV Bhuj-Gadh | 10 GD-1 WR 20-10-2025 21:51 21-10-2025 04:15 06:24 1.2 - 0.00% - 54407 47271 Complete outage of 220 kV Gadsisa S/S: At 21:51 Hrs/20-10-2025, 220kV Bhuj–Gadhsisa line tripped due to B phase to ground fault (CT jumper opened at Bhuj end), fault current- 23.8KA, 1.01 km from Bhuj end. 1 220kV Bhuj-Gadhsisa S/C 2 220kV Gadhsisa Bus-1 3 220kV Gadhsisa Bus-2 4 220/33 kV 160MVA Gadhsisa ICT-1 | grid_india_gd/grid_events/2025-10-01
G00009 | 2025-10 | 24 | GD-1 | WR |  |  | 2025-10-21T03:58 | 2025-10-21T04:29 | 0.52 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GD-1 WR 21-10-2025 03:58 21-10-2025 04:29 00:31 - - - - 51637 44133 Partial outage of 400 kV Nicol S/S: At 03:58 hrs/21-10-2025, The 400 kV PIRANA–NICOL-II–1 and 400 kV RANCHODPURA–NICOL-II–1 lines tripped on overvoltage. Subsequently, for load changeover at Nicol, the 400/132 kV ICTs were manual | 11 GD-1 WR 21-10-2025 03:58 21-10-2025 04:29 00:31 - - - - 51637 44133 Partial outage of 400 kV Nicol S/S: At 03:58 hrs/21-10-2025, The 400 kV PIRANA–NICOL-II–1 and 400 kV RANCHODPURA–NICOL-II–1 lines tripped on overvoltage. Subsequently, for load changeover at Nicol, the 400/132 kV ICTs were manually opened by the station, resulting in the 400 kV bus at Nicol becoming dead. 1 400 kV PIRANA–NICOL-II–1 2 400 kV RANCHODPURA–NICOL-II–1 3 400/132 KV ICT 1 4 400/132 KV ICT 2 5 400/132 KV ICT 3 | grid_india_gd/grid_events/2025-10-01
G00010 | 2025-10 | 10 | GI-2 | Uttar Pradesh | UP | Northern | 2025-10-21T19:16 | 2025-10-21T20:03 | 0.78 | 0 | 109 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-2 Uttar Pradesh 21-10-2025 19:16 21-10-2025 20:03 00:47 0 109 0.000 0.221 42847 49218 i) 400/220kV Agra(UP) S/s has double main and transfer bus scheme at both 400kV & 220kV level and double bus scheme at 132kV level. During antecedent condition, 400/220kV 500MVA ICT-2, 315 MVA ICT-3, 220kV fe | 10 GI-2 Uttar Pradesh 21-10-2025 19:16 21-10-2025 20:03 00:47 0 109 0.000 0.221 42847 49218 i) 400/220kV Agra(UP) S/s has double main and transfer bus scheme at both 400kV & 220kV level and double bus scheme at 132kV level. During antecedent condition, 400/220kV 500MVA ICT-2, 315 MVA ICT-3, 220kV feeder to IOCL-I, Agra220kV-I, Gokul-I & 220/132kV ICT-6 were connected to 220kV Bus-1 and rest of the elements were connected to 220kV Bus-2 at Agra(UP) . ii) As reported, at 19:16 hrs, R & Y phase CT of 220kV Agra-IOCL line-1 at Agra end damaged. Distance protection at Agra end operated in Z-1 however, due to delay in decay of complete fault current, LBB protection operated. Current more than 200 Amp persisted for more than 200msec. iii) Due to LBB protection operation, all the elements connected to 220kV Bus-1 i.e., 400/220kV 500MVA ICT-2, 315 MVA ICT-3, 220kV feeder to IOCL-I, Agra220kV-I, Gokul-I & 220/132kV ICT-6 at Agra(UP) tripped. iv) At the same time, due to tripping of 500 MVA ICT-2 and 315 MVA ICT-3, case-5 of SPS of transformers at Agra(UP) operated. 220kV feeder to Agra220kV-II, IOCL-II and 132kV feeders to Foundry Nagar, Sadabad, Agra Taj, Dayalbagh-I & Bhimnagri tripped on SPS operation. 220kV feeder to Shamsabad and Mitai didn’t trip on SPS. During inspection, it was found that CB status of both the feeders was not showing in SPS system. v) Further, at 19:16:16 hrs, 400/220kV 500 MVA ICT-1 at Agra(UP) also tripped on differential protection operation. As reported, no | grid_india_gd/grid_events/2025-10-01
G00011 | 2025-10 | 25 | GI-2 | WR |  |  | 2025-10-21T20:03 | 2025-10-21T21:14 | 1.18 | 726 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 1150 MW occurred in Maharashtra control area and No load loss reported. | 12 GI-2 WR 21-10-2025 20:03 21-10-2025 21:14 01:11 726 - 1.11% - 65530 52355 Partial outage of 400 kV Chandrapur S/S: 1. At 20:03 hrs. Disturbance occurred in Chandrapur, Dhariwal & Bhadrawati: Y phase IPS tube (bus isolator to CB) of 400 kV Chandrapur-II-Chandrapur Switching ckt-2 fell down at Chandrapur II end and created Y-E fault. As the fault was not cleared by primary protection (600 ms delay observed), multiple lines connected to 400kV Chandrapur-II tripped from the respective remote ends on Zone 2 DPR operation. 2. During this event at Bhadrawati HVDC, three AC lines on the west side tripped due to overvoltage (464kV as per PMU). The auxiliary supply was disturbed, resulting in tripping of both HVDC poles. 3. Chandrapur Unit 8 & 9 (500 MW each), Dhariwal Units 1 & 2 (300 MW each) tripped. With the tripping of units, multiple lines at Chandrapur & Dhariwal tripped on Over Voltage protection operation. 4. 400kV Chandrapur switching station has become dead due to tripping of respective lines and units. 5. Generation loss of 1150 MW occurred in Maharashtra control area and No load loss reported. 1 400 kV-Chandrapur-Chandrapur-II-1 & 2 2 400 kV-Chandrapur II-Bus-1 3 400 kV Dhariwal-Chandrapur-II-1 & 2 4 400 kV Dhariwal-Parli(PG)-1 5 400 kV Chandrapur-II-Warora-1 & 2 6 400 kV Bhadrawati-Raipur-1 & 3 7 400 kV Bhadrawati-Chandrapur-II-1 8 400 kV Bhadrawati-GMR Warora-1 9 400 kV Bhilai-Bhadrawati-1 10 400 kV Chandrapur-II-Nanded-1 & 2 11 400 kV Chandrapur-Khaperkheda-1 12 400 | grid_india_gd/grid_events/2025-10-01
G00012 | 2025-10 | 26 | GD-1 | WR |  |  | 2025-10-22T23:17 | 2025-10-28T01:00 | 121.72 | 37 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 37 MW occurred due to loss of evacuation. | 13 GD-1 WR 22-10-2025 23:17 28-10-2025 01:00 121:43 37 - 0.06% - 59438 48866 Complete outage of 220 kV Gadsisa S/S: At 23:17 Hrs/22-10 2025, 220kV Bhuj–Gadhsisa line tripped due to B phase to ground fault. Indications at Gadsisa end, 31 km, 0.8 kA. At Bhuj end, 38.7 km, 4.94 kA. Generation loss of 37 MW occurred due to loss of evacuation. After patrolling, tower collapse is observed in tower no. 21/4 and 21/5. 1. 220kV Bhuj-Gadhsisa S/C 2. 220kV Gadhsisa Bus-1 3. 220kV Gadhsisa Bus-2 4. 220/33 kV 160MVA Gadhsisa ICT-1 | grid_india_gd/grid_events/2025-10-01
G00013 | 2025-10 | 27 | GD-1 | WR |  |  | 2025-10-29T04:41 | 2025-10-29T06:58 | 2.28 | 18 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 18 MW occurred due to loss of evacuation path. | 14 GD-1 WR 29-10-2025 04:41 29-10-2025 06:58 02:17 18 - 0.03% - 55579 46822 Complete outage of 220 kV Teq Green S/S: At 04:41 Hrs/29-10-2025, 220kV Kallam–TEQ_GREEN line tripped due to B phase to ground fault. Generation loss of 18 MW occurred due to loss of evacuation path. 1 220kV Kallam–TEQ_GREEN Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 KARNATAKA 03-10-2025 15:55 03-10-2025 16:09 00:14 0 208 0.0 % 0.0 % 48620.7 54371.57 Complete outage of 220kV TATAGUNI, KIADB-HAROHALLI and KANKAPURA and Tripping of Bus-A1 of SOMANAHALLI station. The triggering incident is the Y-G bus fault occurred in Somanahally-Harohally line bay due to failure of Y phase cross bus insulator string before the CT of the line (can be confirmed from the DR of Somanahally-Harohally line at Somanahally). Since the BBP is in disabled condition and BBP protection in not available, multiple lines tripped on Z4 and 500MVA Somanahally ICT-1 tripped on OC protection operation and led to the Complete outage of KIADB-HAROHALLI and KANKAPURA station. The even led to the Complete outage of 220kV TATAGUNI, KIADB-HAROHALLI and KANKAPURA and Tripping of Bus-A1 of SOMANAHALLI station. 220KV-HAROHALLI-SOMANAHALLI-1, 220KV-TATAGUNI- SOMANAHALLI-1, 220KV-SOMANAHALLI-ELECTRONIC_CITY-1, 400KV/220KV SOMANAHALLI-ICT-1, 220KV-TATAGUNI- VRISHABHAVATHI_VALLEY-1 2 GD - 1 KARNATAKA 04-10-2025 | grid_india_gd/grid_events/2025-10-01
G00014 | 2025-10 | 11 | GD-1 | Punjab | PB | Northern | 2025-10-29T14:59 | 2025-10-29T15:18 | 0.32 | 590 | 35 | FALSE | FALSE | FALSE | FALSE | FALSE | vii) As per SCADA change in demand of approx 35 MW in Punjab control area and generation loss of approx 590 MW at GGSTPS (Ropar TPS) is observed. | 11 GD-1 Punjab 29-10-2025 14:59 29-10-2025 15:18 00:19 590 35 1.313 0.069 44939 51069 i) 220/132kV GGSTPS (Ropar TPS) has 3 main bus and 1 reserve bus. During antecedent condition, 220kV Bus-I&II were already under shutdown for ongoing construction work in switchyard. 220kV feeders to Ghulal, Jadla-I&II, Ropar400-I&III, Khara, 210 MW Unit-3 & 6, ST-3 & 4 and 100MVA ICT-1&2 were connected to 220kV Reserve bus and remaining feeders and 210 MW Unit-4 & 5 were connected to 220kV Bus-2. 210 MW Unit-1&2 were under shutdown and 220kV Gobindgarh-I feeder was also taken under shutdown to attend air leakage from the compressor. ii) During antecedent condition, 210 MW Unit-3,4,5&6 at GGSTPS were running and generating ~146 MW , ~147 MW , ~142 MW & ~153 MW respectively. iii) As reported, at 14:59 hrs, while hanging earth stick on 220kV Gobindgarh-I feeder, the earth stick inadvertently got induction voltage from the nearby live feeder of Interlinking 220/132kV 100MVA Transformer-2 and created bus fault. iv) On this fault, bus bar protection of 220kV Reserve bus (bus bar Z-4) operated leading to tripping of all the elements connected to 220kV Reserve bus. v) At the same time, 210 MW Unit-4 & 5 which were connected to 220kV Bus-3 also tripped due to tripping of allied auxiliaries running on ST-3 and ST-4. vi) As per PMU at Nallagarh(PG) , R-N fault which cleared within 100msec is observed. vii) As per SCADA change in demand of approx 35 MW in Punjab control area and generation loss of appr | grid_india_gd/grid_events/2025-10-01
G00015 | 2025-10 | 12 | GI-2 | Punjab | PB | Northern | 2025-10-30T12:58 | 2025-10-30T14:17 | 1.32 | 0 | 245 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-2 Punjab 30-10-2025 12:58 30-10-2025 14:17 01:19 0 245 0.000 0.479 44554 51164 i) 400/220kV Ludhiana(PG) has one & half breaker scheme at 400kV level and double main & transfer bus scheme at 220kV level. ii) During antecedent condition, 400/220kV ICT-1, 2, 3 & 4 were carrying ~181 MW, 169 MW, | 12 GI-2 Punjab 30-10-2025 12:58 30-10-2025 14:17 01:19 0 245 0.000 0.479 44554 51164 i) 400/220kV Ludhiana(PG) has one & half breaker scheme at 400kV level and double main & transfer bus scheme at 220kV level. ii) During antecedent condition, 400/220kV ICT-1, 2, 3 & 4 were carrying ~181 MW, 169 MW, 111 MW & 168 MW respectively. iii) As reported, at 12:58 hrs, flashover occurred in R & Y phase bus isolators of 206 bay (ICT-4 bay) . This happened during onload operation of 86B isolator of 206 bay (ICT-4 bay) . iv) On this fault bus bar protection of both the 220kV Bus-1&2 operated leading to tripping of all the elements connected to 220kV bus-1&2 at Ludhiana(PG) . v) From the event logger record, it was observed that prior to BB tripping, condition of Zone Merge was formed which has resulted in extending tripping in both Busbars. At 12:49:51:149, DC earth fault in source-1 is observed in event list. vi) As per PMU at Ludhiana(PG) , R-Y double phase fault which cleared within 120msec is observed. vii) As per SCADA change in demand of approx 245 MW in Punjab control area is observed. viii) As a precautionary measure, AC & DC supply of all 220kV isolators has been kept OFF. Further investigation is under progress. Suspected cause of tripping is currently attributable to 206 Schnieder make BCU i.e., maloperation of BO card) 1) 220kV Bus-1 at Ludhiana(PG) 2) 220kV Bus-1 at Ludhiana(PG) 3) 400/220kV 500 MVA ICT-1 at Ludhiana(PG) 4) 400/220kV 500 MVA ICT-2 at Ludhiana(PG) 5) 400/220kV | grid_india_gd/grid_events/2025-10-01
G00016 | 2025-10 | 13 | GI-2 | Haryana | HR | Northern | 2025-10-31T06:02 | 2025-10-31T07:12 | 1.17 | 0 | 440 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 400/220kV 315 MVA ICT-1 at Daulatabad(HR) 2) 400/220kV 315 MVA ICT-2 at Daulatabad(HR) 3) 400/220kV 315 MVA ICT-3 at Daulatabad(HR) 4) 400/220kV 315 MVA ICT-4 at Daulatabad(HR) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 13 GI-2 Haryana 31-10-2025 06:02 31-10-2025 07:12 01:10 0 440 0.000 0.962 34273 45736 i) 400/220kV Daulatabad(HR) has one & half breaker scheme at 400kV level and double main bus scheme at 220kV level. ii) During antecedent condition, 400/220kV ICT-1, 2, 3 & 4 were carrying 83 MW, 82 MW, 82 MW & 84 MW respectively. iii) As reported, at 06:02 hrs, B-ph CT of 220kV bus coupler burst resulting into 220kV bus fault. iv) As bus bar protection was not in working condition due to issue in cables, bus bar protection didn’t operate and fault cleared with the tripping of all four 400/220kV 315 MVA ICTs at Daulatabad(HR) . v) As per PMU at Gurgaon(PG) , B-N fault with delayed clearance of 660 msec is observed. vi) As per SCADA change in demand of approx 440 MW in Haryana control area is observed. vii) As reported by Daulatabad(HR) , issues with the bus bar protection has already been taken up with the relay OEM. 1) 400/220kV 315 MVA ICT-1 at Daulatabad(HR) 2) 400/220kV 315 MVA ICT-2 at Daulatabad(HR) 3) 400/220kV 315 MVA ICT-3 at Daulatabad(HR) 4) 400/220kV 315 MVA ICT-4 at Daulatabad(HR) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2025-10-01
G00017 | 2025-11 | 8 | GD-1 | Madhya Pradesh | MP | Western | 2025-11-01T01:30 | 2025-11-01T03:06 | 1.6 | 732 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of both units, generation loss of 732 MW occurred at JP Nigrie S/S. | 1 GD-1 Madhya Pradesh 01-11-2025 01:30 01-11-2025 03:06 01:36 732 0 1.22% 0.00% 60139 47909 Complete outage of 400 kV JP Nigrie S/S: At 01:30 hrs /01-11-2025, 400 kV Satna- JP Nigrie 1 tripped on R ph-E fault after auto-reclose attempt. The Ckt-2 also tripped at the same time. Since the evacuating lines were lost, the Units 1 & 2 at JP Nigrie tripped and the 400 kV JP Nigrie S/S became dark. Due to tripping of both units, generation loss of 732 MW occurred at JP Nigrie S/S. 1. 400 kV Satna- JP Nigrie 1 2. 400 kV Satna- JP Nigrie 2 3. 400 kV JP Nigrie bus-1 4. 400 kV JP Nigrie bus-2 5. JP Nigrie Unit 1 (660 MW) | grid_india_gd/grid_events/2025-11-01
G00018 | 2025-11 | 19 | GI-2 | Andhra Pradesh | AP | Southern | 2025-11-01T12:39 | 2025-11-01T19:53 | 7.23 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 6 GI-2 Andhra Pradesh 01-11-2025 12:39 01-11-2025 19:53 07:14 0 0 0.0 % 0.0 % 44970.56 46996.56 Tripping of 765kV Bus-2 of 765kV Nellore Pooling Station of PGCIL SR-1 As per the reports submitted, the triggering incident was R-B fault in 765kV Nellore PS Bus-2 caused due to insulator failure on bus bar. Immediately, 765kV Bus-2 BBP operated and all main breakers connected to 765kV Bus-2 tripped. NPS - 765KV - Bus 2 Details of Grid Events during the Month of November 2025 in Southern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2025-11-01
G00019 | 2025-11 | 1 | GI-1 | Rajasthan | RJ | Northern | 2025-11-05T01:11 | 2025-11-05T02:36 | 1.42 | 480 | 178 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-1 Rajasthan 05-11-2025 01:11 05-11-2025 02:36 01:25 480 178 1.60% 0.45% 29960 39395 i)220/132kV Kota Sakatpura(RS) has four buses with double main bus scheme at 220kV level. 220kV Bus-A&B are with sectionaliser and Bus-C & D are parallel bus. ii)During antecedent condition, 220/132kV 160 MVA Tr | 1 GI-1 Rajasthan 05-11-2025 01:11 05-11-2025 02:36 01:25 480 178 1.60% 0.45% 29960 39395 i)220/132kV Kota Sakatpura(RS) has four buses with double main bus scheme at 220kV level. 220kV Bus-A&B are with sectionaliser and Bus-C & D are parallel bus. ii)During antecedent condition, 220/132kV 160 MVA Transformer-1 and 100 MVA Transformer-3&4 and 220kV feeders to RAPS-B, KTPS-3&4 were connected at 220kV Bus-C. Other elements were on another buses. iii)As reported, at 01:11 hrs, Y-ph CT at 220kV side of 220/132kV 100 MVA Transformer-4 burst leading to bus fault on 220kV Bus-C. iv)On this fault, bus bar protection of Bus-C operated resulting into tripping of all the elements connected to 220kV Bus-C along with the bus coupler breaker. v)As per DR of bus bar relay, Y-N fault converted into R-Y fault with delayed clearance ~240 msec is observed. vi)As per PMU at Kota(PG), Y-N fault converted into R-Y fault with delayed clearance ~320 msec is observed vii)At the same time, 220kV Kota Sakatpura-RAPS_A line-2 also tripped from Kota Sakatpura end on Z-4 distance protection operation. Further, 220kV kota Saktpura- Anta line, 220kV Kota Sakatpura-KTPS line-2 along with 210 MW unit-3,4&5 at KTPS also tripped. Reason of multiple elements tripping at KTPS yet to be received. viii)As per SCADA change in demand of approx 178 MW in Rajasthan control area and loss in generation of ~480 MW at KTPS is observed 1)220 KV RAPS_B(NP)- Kota Sakatpura(RS) (RS) Ckt 2)220kV Kota Sakatpura-KTPS ckt-3 3)220kV | grid_india_gd/grid_events/2025-11-01
G00020 | 2025-11 | 9 | GD-1 | Maharashtra | MH | Western | 2025-11-06T17:04 | 2025-11-06T17:23 | 0.32 | 0 | 96 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Maharashtra 06-11-2025 17:04 06-11-2025 17:23 00:19 0 96 0.00% 0.16% 68570 60119 Complete outage of 220 kV Colorchem S/S: 220 kV Kalwa-DCHI was under S/D for conductor replacement work. Temporary arrangement was made by tapping 220 kV Kalwa- Temghar line between 220 kV DCHI and 220 kV Colorch | 2 GD-1 Maharashtra 06-11-2025 17:04 06-11-2025 17:23 00:19 0 96 0.00% 0.16% 68570 60119 Complete outage of 220 kV Colorchem S/S: 220 kV Kalwa-DCHI was under S/D for conductor replacement work. Temporary arrangement was made by tapping 220 kV Kalwa- Temghar line between 220 kV DCHI and 220 kV Colorchem. At 17:04 Hrs/ 06-11-2025, 220 kV Kalwa-T point- Colorchem, 220 kV Kalwa-T point-DCHI, 220 kV Temghar-Tpoint- DCHI and 220 kV Temghar-T point- Colorchem lines tripped on Y-B phase fault due to kite string struck between Y&B phases. 1 I. 220 kV Kalwa-T point- Colorchem, II. 220 kV Kalwa-T point-DCHI, III. 220 kV Temghar-Tpoint-DCHI IV. 220 kV Temghar-T point- Colorchem lines 2 220 kV Colorchem- Temghar | grid_india_gd/grid_events/2025-11-01
G00021 | 2025-11 | 2 | GD-1 | Rajasthan | RJ | Northern | 2025-11-07T13:40 | 2025-11-07T14:14 | 0.57 | 60 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | iv)As per PMU at Fatehgarh_III(PG), no fault and fluctuation in voltage was observed in the system v)As per PMU MW data of RSJPL, solar generation loss of ~60 MW observed at RSJPL Restation. | 2 GD-1 Rajasthan 07-11-2025 13:40 07-11-2025 14:14 00:34 60 0 0.14% 0.00% 44306 48465 i)Generation of 220kV Renew Surya Jyoti Pvt Ltd. (RSJPL) (IP) station evacuates through 220 KV RSJPL-Fatehgarh_III line. ii)During antecedent condition, 220kV RSJPL(IP) station was generating approx 60 MW (as per PMU). iii)As reported, at 13:40 hrs, 220kV Fatehgarh_III-RSJPL line tripped on earth fault. iv)As per PMU at Fatehgarh_III(PG), no fault and fluctuation in voltage was observed in the system v)As per PMU MW data of RSJPL, solar generation loss of ~60 MW observed at RSJPL Restation. As per SCADA, no significant change in NR solar generation loss is observed. 1)220kV Fatehgarh_III-RSJPL line | grid_india_gd/grid_events/2025-11-01
G00022 | 2025-11 | 3 | GI-1 | Jammu and Kashmir | JK | Northern | 2025-11-10T16:24 | 2025-11-10T17:34 | 1.17 | 0 | 180 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GI-1 Jammu and Kashmir 10-11-2025 16:24 10-11-2025 17:34 01:10 0 180 0.00% 0.38% 41245 47244 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 were carrying 73 MW and 64 MW respectively (a | 3 GI-1 Jammu and Kashmir 10-11-2025 16:24 10-11-2025 17:34 01:10 0 180 0.00% 0.38% 41245 47244 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 were carrying 73 MW and 64 MW respectively (as per SCADA). iii)As reported, at 16:24 hrs, 132 KV CT of B-ph Bus coupler bay blasted. During the same time, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 tripped from Salal end (exact nature and location of fault yet to be shared). iv)As per DR at Salal(NH) end, B-N fault converted to R-B-N fault again converted to R-Y-B fault occurred. Fault current was Ir=~2.105kA, Iy=~2.148kA, Ib=~2.036kA from Salal end for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 and Ir=~1.852kA, Iy=~1.951kA, Ib=~1.877kA from Salal end for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-2. Fault sensed in zone-3 at Salal end. Line tripped from Salal end after zone-3 time delay. v)As per PMU at Kishenpur(PG), R-B phase to phase fault converted to 3-phase fault was observed with delayed fault clearing time of 1040ms. vi)As per SCADA, change in demand of approx 180 MW is observed in J&K control area. 1) 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 2) 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-2 | grid_india_gd/grid_events/2025-11-01
G00023 | 2025-11 | 10 | GD-1 | Maharashtra | MH | Western | 2025-11-14T02:21 | 2025-11-14T03:23 | 1.03 | 425 | 26 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to the event 26 MW load loss and 425 MW Generation loss occurred. | 3 GD-1 Maharashtra 14-11-2025 02:21 14-11-2025 03:23 01:02 425 26 0.76% 0.06% 55587 47100 Complete outage of 220 kV Uran S/S: At 02:21 Hrs /14.11.2025, 220 kV Uran S/S got dead due to tripping of 220 kV Bus 1&2 and all connected elements on Bus bar protection due to fire in R phase CT of Bus Coupler. Due to the event 26 MW load loss and 425 MW Generation loss occurred. 1. 220 kV Uran–Apta 1 2. 220 kV Uran–Apta 2 3. 220 kV Uran–Apta 3 4. 220 kV Uran–Apta 4 5. 220kV Uran Bus-1 6. 220kV Uran Bus-2 | grid_india_gd/grid_events/2025-11-01
G00024 | 2025-11 | 4 | GD-1 | Delhi | DL | Northern | 2025-11-14T16:35 | 2025-11-14T16:47 | 0.2 | 0 | 130 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 4 GD-1 Delhi 14-11-2025 16:35 14-11-2025 16:47 00:12 0 130 0.00% 0.27% 43965 48630 i)220/66/33kV Gopalpur(DTL) has double main Bus arrangement at 220kV side. 220kV Gopalpur- SOWazirabad D/C was in open condition from Gopalpur end. ii)During antecedent condition, 220kV Bus-2 at Gopalpur(DTL) was taken into outage due to some protection related work on 220kV Gopalpur-Timarpur Ckt. iii)As reported, at 16:35 hrs, bus bar protection operated at 220kV Bus-1 at Gopalpur(DTL) during carrying out protection work on 220kV Gopalpur-Timarpur Ckt (exact reason yet to be shared). iv)Due to bus bar protection operation, all the 220kV elements connected to 220kV Bus-1 at Gopalpur(DTL) tripped and complete blackout occurred at 220/66/33kV Gopalpur(DTL) S/s. v)At 16:47 hrs, 220kV Gopalpur- SOWazirabad Ckt-2 was taken into service to charge 220kV Gopalpur(DTL) S/s. vi)As per PMU at Mandola(PG), no fault was observed in the system. vii)As per SCADA, change in demand of approx 130 MW in Delhi control area is observed. 1) 220 KV Mandola(PG)-Gopalpur(DTL) (DTL) Ckt-1 2) 220 KV Mandola(PG)-Gopalpur(DTL) (DTL) Ckt-2 3) 220 KV Gopalpur-Sabzi Mandi (DTL) Ckt-1 4) 220/33kV 100 MVA ICT-1 at Gopalpur(DTL) 5) 220/66kV 100 MVA ICT-2 at Gopalpur(DTL) 6) 220/33kV 100 MVA ICT-3 at Gopalpur(DTL) 7) 220/66kV 160 MVA ICT-4 at Gopalpur(DTL) Details of Grid Events during the Month of November 2025 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Rest | grid_india_gd/grid_events/2025-11-01
G00025 | 2025-11 | 11 | GD-1 | Gujarat | GJ | Western | 2025-11-18T17:47 | 2025-11-18T19:35 | 1.8 | 58 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 58 MW occurred due to loss of evacuation path at 220kV-Roha-Naranpar. | 4 GD-1 Gujarat 18-11-2025 17:47 18-11-2025 19:35 01:48 58 0 0.08% 0.00% 73465 64903 Complete outage of 220 kV Roha Naranpar S/S: At 17:47hrs /18-11-2025, 220 kV Bhuj- Roha-Naranpar GIWEL(Wind RE) single circuit tripped on Bph-E fault. Due to tripping of line, both 220 kV buses at 220kV-Roha-Naranpar were de-energised. Generation loss of 58 MW occurred due to loss of evacuation path at 220kV-Roha-Naranpar. 1. 220 kV Bhuj-Roha-Naranpar 2. 220 kV Roha-Naranpar BUS-1 3. 220 kV Roha-Naranpar BUS-2 4. 220 kV Roha-Naranpar ICT-1 5. 220 kV Roha-Naranpar ICT-2 | grid_india_gd/grid_events/2025-11-01
G00026 | 2025-11 | 5 | GI-2 | Jammu and Kashmir | JK | Northern | 2025-11-21T11:51 | 2025-11-21T12:16 | 0.42 | 0 | 130 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GI-2 Jammu and Kashmir 21-11-2025 11:51 21-11-2025 12:16 00:25 0 130 0.00% 0.22% 55236 59513 i)400/220kV Kishenpur(PG) S/s has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)During antecedent condition, 400 KV Kishenpur-Moga (PG) Ckt-1 &2 were | 5 GI-2 Jammu and Kashmir 21-11-2025 11:51 21-11-2025 12:16 00:25 0 130 0.00% 0.22% 55236 59513 i)400/220kV Kishenpur(PG) S/s has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)During antecedent condition, 400 KV Kishenpur-Moga (PG) Ckt-1 &2 were carrying 771 MW and 744 MW respectively (as per SCADA). iii)As reported, at 11:51 hrs, 400 KV Kishenpur-Moga (PG) Ckt-2 tripped on permanent Y-N phase to earth fault due to Y-phase jumper broken near Kishenpur(PG) S/s. As per DR, fault current was 13.41 kA and fault distance was 3.6 km from Kishenpur(PG) end; fault (with unsuccessful A/R) sensed in zone-1 and Main-II relay operated at Kishenpur(PG) end. iv)On the same fault, 400 KV Kishenpur-Moga (PG) Ckt-1 also tripped from Kishenpur(PG) end only. As per DR, fault current was 2.07 kA from Kishenpur(PG) end; fault sensed in zone-4 and Main-II relay operated at Kishenpur(PG) end. v)During investigation, it was observed that after Z4 pickup, D60 (Main-II) relay issued 3ph tripping due to “TRIPBUS-1 optd”. On examining seƫng parameters, it was observed that input setting parameters to Trip Bus 1 function had been assigned for “Z2,Z3 and Z4 pickup” whereas as per standard template inputs to Trip Bus function should be assigned for “Z2,Z3 and Z4 operated”. vi)As corrective action taken, seƫng in D60 relay was corrected and implemented as per standard template. vii)As per PMU at Kishenpur(PG), Y-N phase to earth fault with unsuccessful | grid_india_gd/grid_events/2025-11-01
G00027 | 2025-11 | 6 | GD-1 | Jammu and Kashmir | JK | Northern | 2025-11-22T19:44 | 2025-11-22T21:05 | 1.35 | 0 | 80 | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GD-1 Jammu and Kashmir 22-11-2025 19:44 22-11-2025 21:05 01:21 0 80 0.00% 0.15% 45535 52726 i)220/33kV Chowadhi(JK) S/s has double main and transfer bus scheme at 220kV side and two 220kV lines are connected: 220 KV Samba(PG)-Chowadhi (JK) (PDD JK) Ckt and 220 KV Chowadhi (JK)-Gladni(PDD) (PDD JK) | 6 GD-1 Jammu and Kashmir 22-11-2025 19:44 22-11-2025 21:05 01:21 0 80 0.00% 0.15% 45535 52726 i)220/33kV Chowadhi(JK) S/s has double main and transfer bus scheme at 220kV side and two 220kV lines are connected: 220 KV Samba(PG)-Chowadhi (JK) (PDD JK) Ckt and 220 KV Chowadhi (JK)-Gladni(PDD) (PDD JK) Ckt. ii)As reported, at 19:44 hrs, 220 KV Samba(PG)-Chowadhi (JK) (PDD JK) Ckt tripped on permanent R-N phase fault (unsuccessful A/R) due to R-phase conductor snapped. As per DR at Samba end, fault current was 2.273kA (4.134kA during A/R) from Samba(PG) end; zone-1 distance protection (Main-II) operated at Samba(PG) end. As per DR at Chowadhi end, zone-2 distance protection (Main-I) operated at Chowadhi(JK) end. Carrier sent from Samba(PG), but not received at Chowadhi(JK) (Carrier communication issue observed). iii)On the same fault, 220 KV Chowadhi (JK)-Gladni(PDD) (PDD JK) Ckt also tripped from Chowadhi(JK) end only. As per DR, zone-4 distance protection operated at Chowadhi end (Main-II) and fault sensed in zone-3 at Jammu/Gladini end. iv)During investigation, it was observed that zone-4 delay at Chowadhi(JK) end of 220 KV Chowadhi (JK)-Gladni(PDD) (PDD JK) Ckt and zone-2 delay at Chowadhi(JK) end of 220 KV Samba(PG)-Chowadhi (JK) (PDD JK) Ckt were same (500 ms). v)As per PMU at Kishenpur(PG), R-N phase to earth fault with unsuccessful A/R was observed with fault clearing time of 120ms. vi)As per SCADA, change in demand of approx 80 MW is observed in J&K control area. 1) 220 | grid_india_gd/grid_events/2025-11-01
G00028 | 2025-11 | 12 | GD-1 | Gujarat | GJ | Western | 2025-11-24T04:00 | 2025-11-24T05:17 | 1.28 | 125 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | No generation loss due to the event. | 5 GD-1 Gujarat 24-11-2025 04:00 24-11-2025 05:17 01:17 125 0 0.22% 0.00% 56614 50000 Complete outage of 400 kV Khavda PSS-1 S/S: At 04:00 Hrs /24-11-2025, 400 kV Khavda PSS 1 went dead due B-phase fault in the 89 A gas compartment of 400/33 kV Khavda PSS 1 ICT 4. Consequently, the 400 kV Khavda PSS1 – Khavda PS1 line, and all four 400/33 kV ICTs at Khavda PSS 1 (ICTs 1, 2, 3 & 4) tripped on bus-bar protection operation. No generation loss due to the event. Simultaneously, due to the disturbance, the 765/400 kV Khavda PS 1 ICT 7 tripped on B-phase differential protection. As a result of ICT 7’s tripping, a sudden voltage rise was observed at Khavda PS1. 1. 400 kV Khavda PSS 1 Bus 1 2. 400 kV Khavda PSS1- Khavda PS1 3. 400/33 kV Khavda PSS 1 ICT1 4. 400/33 kV Khavda PSS 1 ICT 2 5. 400/33 kV Khavda PSS 1 ICT3 6. 400/33 kV Khavda PSS 1 ICT 4 7. 765/400 kV Khavda PS1 ICT 7 8. 400 kV Asoj- Wanakbori 9. 400 kV Nicol- Ranchodpura | grid_india_gd/grid_events/2025-11-01
G00029 | 2025-11 | 13 | GD-1 | Gujarat | GJ | Western | 2025-11-24T14:06 | 2025-11-24T16:10 | 2.07 | 600 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 600 MW occurred at 400 kV NTPC PSS2 S/S. | 6 GD-1 Gujarat 24-11-2025 14:06 24-11-2025 16:10 02:04 600 0 0.82% 0.00% 73096 65684 Complete outage of 400 kV NTPC Khavda PSS-2 S/S: At 14:06 hrs/ 24-11-2025, 400 kV NTPC PSS2–KPS2 line tripped due to a three-phase fault caused by foreign material (polythene). Generation loss of 600 MW occurred at 400 kV NTPC PSS2 S/S. 1. 400 kV NTPC PSS 2 –KPS2 2. 400/33 kV NTPC PSS 2 ICT1 3. 400/33 kV NTPC PSS 2 ICT 2 4. 400/33 kV NTPC PSS 2 ICT3 5. 400/33 kV NTPC PSS 2 ICT 4 6. 400/33 kV NTPC PSS 2 ICT 5 | grid_india_gd/grid_events/2025-11-01
G00030 | 2025-11 | 14 | GD-1 | Gujarat | GJ | Western | 2025-11-25T11:52 | 2025-11-25T17:02 | 5.17 | 571 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 572 MW occurred at 400 kV NTPC PSS2 due to loss of the evacuation path which led to the substation blackout. | 7 GD-1 Gujarat 25-11-2025 11:52 25-11-2025 17:02 05:10 571 0 0.75% 0.00% 75949 69297 Complete outage of 400 kV NTPC Khavda PSS-2 S/S: At 11:52 Hrs/ 25-11-2025, 400 kV NTPC PSS2–Khavda PS2 line tripped on R-E fault due differential protection operated on both ends of line. Generation loss of 572 MW occurred at 400 kV NTPC PSS2 due to loss of the evacuation path which led to the substation blackout. 1. 400 kV NTPC PSS 2 –KPS2 2. 400/33 kV NTPC PSS 2 ICT1 3. 400/33 kV NTPC PSS 2 ICT 2 4. 400/33 kV NTPC PSS 2 ICT3 5. 400/33 kV NTPC PSS 2 ICT 4 Elements Tripped Details of Grid Events during the Month of November 2025 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of November 2025 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of lo | grid_india_gd/grid_events/2025-11-01
G00031 | 2025-11 | 15 | GD-1 | Gujarat | GJ | Western | 2025-11-29T00:52 | 2025-11-29T09:53 | 9.02 | 127 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss (Wind) of 127 MW occurred due to loss of evacuation path. | 8 GD-1 Gujarat 29-11-2025 00:52 29-11-2025 09:53 09:01 127 0 0.20% 0.00% 61966 52398 Complete outage of 400 kV NTPC Khavda PSS-3 S/S: At 00:52 Hrs /29-11-2025, 400 kV Khavda PSS3- Khavda PS1 line tripped on R-phase fault. Generation loss (Wind) of 127 MW occurred due to loss of evacuation path. 765/400 kV Khavda PS 1 ICT-7 also tripped at the same time due to differential protection operation. 1. 400 kV Khavda PSS3- Khavda PS1 2. 400 kV Khavda PSS3 Bus-1 3. 400 kV Khavda PSS3 Bus-2 4. 400/33 kV Khavda PSS3 ICT-1 5. 400/33 kV Khavda PSS3 ICT-2 6. 400/33 kV Khavda PSS3 ICT-3 | grid_india_gd/grid_events/2025-11-01
G00032 | 2025-11 | 7 | GI-1 | Uttar Pradesh | UP | Northern | 2025-11-29T12:12 | 2025-11-29T13:25 | 1.22 | 0 | 210 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220kV Bus-1 at Agra(PG) 2) 220 KV Agra(PG)-Bharatpur(RS) (PG) Ckt 3) 220 KV Agra(PG)-Tundla(UP) (UP) Ckt 4) 220 KV Agra(PG)-Shamshabad(UP) (UP) Ckt 5) 220 KV Agra(PG)-Kirawali(UP) (PG) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 7 GI-1 Uttar Pradesh 29-11-2025 12:12 29-11-2025 13:25 01:13 0 210 0.00% 0.35% 52087 60350 i)765/400/220kV Agra(PG) has double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220kV Bus-2 at Agra(PG) was already under planned outage due to AMP work. Hence all 220kV elements were connected to 220kV Bus-1 at Agra(PG). 400/220kV 315 MVA ICT-1 & 2 at Agra(PG) were carrying approx 175 MW & 195 MW respectively. iii)As reported, at 12:12 hrs, Bus bar protection operated at 220kV Bus-1 at Agra(PG) (exact reason of bus bar protection operation including fault details yet to be shared). iv)Due to bus bar protection operation, all 220kV elements connected at Agra(PG) tripped and 220kV Bus-1 at Agra(PG) became dead. v)As per PMU at Agra(PG), B-N phase to earth fault is observed with fault clearing time of 80 ms. vi)As per SCADA change in demand of approx 70 MW in UP control area and approx 140 MW in Rajasthan control area were observed. 1) 220kV Bus-1 at Agra(PG) 2) 220 KV Agra(PG)-Bharatpur(RS) (PG) Ckt 3) 220 KV Agra(PG)-Tundla(UP) (UP) Ckt 4) 220 KV Agra(PG)-Shamshabad(UP) (UP) Ckt 5) 220 KV Agra(PG)-Kirawali(UP) (PG) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2025-11-01
G00033 | 2025-11 | 16 | GD-1 | Gujarat | GJ | Western | 2025-11-29T16:12 | 2025-11-29T20:30 | 4.3 | 10 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Due to the loss of the evacuation path Generation loss of 10MW occurred at 220kV Sidhpur (Torrent) Wind Power Plant. | 9 GD-1 Gujarat 29-11-2025 16:12 29-11-2025 20:30 04:18 10 0 0.01% 0.00% 77268 68201 Complete outage of 220 kV Sidhpur S/S: At 16:12 hrs/29-11-2025, 220kV Sidhpur-Jamkhambaliya S/C tripped due to Rph-Yph fault. Consequently 220kV Sidhpur s/s blacked out. Due to the loss of the evacuation path Generation loss of 10MW occurred at 220kV Sidhpur (Torrent) Wind Power Plant. 1. 220 KV Jamkhambaliya Sidhpur line 2. 200KV SIDHPUR-BUS 1 3. 200KV SIDHPUR-BUS 2 | grid_india_gd/grid_events/2025-11-01
G00034 | 2025-11 | 17 | GD-1 | Gujarat | GJ | Western | 2025-11-29T16:13 | 2025-11-29T22:36 | 6.38 | 28 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Gneration loss of 28 MW occurred at 220 kV Khakharda due to loss of evacuation path resulted in blackout at power plant. | 10 GD-1 Gujarat 29-11-2025 16:13 29-11-2025 22:36 06:23 28 0 0.04% 0.00% 77243 68241 Complete outage of 220 kV Khakharda(Apraava) S/S: At 16:13 hrs /29-11-2025, 220kV Khakharda -Jamkhambaliya S/C tripped due to Rph-Yph fault. Gneration loss of 28 MW occurred at 220 kV Khakharda due to loss of evacuation path resulted in blackout at power plant. 1. 220kV Jamkhambaliya- Khakharda 2. 220kV Khakharda Bus-1 3. 220kV Khakharda Bus-2 | grid_india_gd/grid_events/2025-11-01
G00035 | 2025-11 | 18 | GD-1 | Madhya Pradesh | MP | Western | 2025-11-30T11:35 | 2025-11-30T12:03 | 0.47 | 270 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of of 270 MW (U6-90.11 MW & U7-179.88MW) occurred at Both S/S due to loss of evacuation path. | 11 GD-1 Madhya Pradesh 30-11-2025 11:35 30-11-2025 12:03 00:28 270 0 0.35% 0.00% 76369 66130 Complete outage of 220 kV Shajapur U6&U7 S/S: At 11:35 Hrs /30-11-2025, 220kV Pachora-Dehripal (U-7) line tripped on Yph differential protection. Due to tripping of this line, Shajapur U7 (Dheripal) & Shajapur U6 (Burley, radially connected with Unit 7) became dark. Generation loss of of 270 MW (U6-90.11 MW & U7-179.88MW) occurred at Both S/S due to loss of evacuation path. 1. 220kV Pachora- Dehripal 2. 220kV Dehripal-Burley 3. 220KV/33KV SHAJAPUR Unit-7(Dehripal)-ICT-1 4. 220KV/33KV SHAJAPUR Unit-7(Dehripal)-ICT-2 5. 220KV/33KV SHAJAPUR Unit-6(Burley)-ICT-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 Karnataka 04-11-2025 07:15 04-11-2025 12:41 05:26 96 50 0.23% 0.10% 41062.68 49777.99 Complete Outage of 220kV Kadra PH and Karwar PH of KPCL 220kV Kadra PH is operating with single bus with Transfer bus. As per the reports submitted, the triggering incident was a three-phase-to-ground fault in the 220 kV Kadra bus. At the Kadra end, Busbar Protection Zone-1 operated, resulting in the tripping of the running Unit-2 and Unit-3, along with all four 220 kV line circuit breakers. This led to complete outage of the 220 kV Kadra Power House (PH). Since the 220 kV Karwar SS is radially fed from the 220 kV Kadra PH, this led to complete outage of 220 kV Karw | grid_india_gd/grid_events/2025-11-01
G00036 | 2025-12 | 1 | GD-1 | Uttar Pradesh | UP | Northern | 2025-12-02T12:25 | 2025-12-02T14:32 | 2.12 | 0 | 110 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 Uttar Pradesh 02-12-2025 12:25 02-12-2025 14:32 02:07 0 110 0.00% 0.18% 55610 61235 i)220/132kV Raebareilly(PG) has double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220 KV Unchahar(NT)-Raebareilly(PG) (PG) Ckt-1 & 2 were under shutdown for line diversion work | 1 GD-1 Uttar Pradesh 02-12-2025 12:25 02-12-2025 14:32 02:07 0 110 0.00% 0.18% 55610 61235 i)220/132kV Raebareilly(PG) has double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220 KV Unchahar(NT)-Raebareilly(PG) (PG) Ckt-1 & 2 were under shutdown for line diversion work by UPPTCL since 02.11.2025 and 220 KV Raebareilly(PG)-C.G. City Ckt was under shutdown since 02.11.2025 for load management of 220 KV Unchahar(NT)-Raebareilly(PG) (PG) Ckt-3 as it is the only source line. 220/132/33 kV Bachravan UPPTCL station was being fed only from 220 KV Raebareilly(PG)-Bachravan(UP) (PG) Ckt.iii)As reported, at 12:25 hrs, Broken conductor alarm was observed at both Raebareilly (PG) and Unchahar(NT) end of 220 KV Unchahar(NT)-Raebareilly(PG) (PG) Ckt-3. Line tripped from Unchahar (NTPC) end only as tripping was enabled on Broken conductor alarm. iv)Since the Broken conductor alarm was observed at both PG and NTPC ends, the Raebareli TLM team was immediately mobilized for emergency patrolling of the line, considering the possibility of conductor or jumper snapping. The TLM team thoroughly patrolled all 37 tension towers (Location 1 to 144), however no abnormalities were reported on the line.v)As at the time of tripping 220kV Bachravan was being fed radially through 220 KV Raebareilly(PG)- Bachravan(UP) (PG) Ckt, the tripping of 220 KV Unchahar(NT)-Raebareilly(PG) (PG) Ckt-3 resulted into loss of source for 220 kV Raebareilly (PG) and 220kV Bachravan. vi)This led | grid_india_gd/grid_events/2025-12-01
G00037 | 2025-12 | 14 | GD-1 | Chhattisgarh | CG | Western | 2025-12-03T10:55 | 2025-12-03T11:57 | 1.03 | 43 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 43 MW occurred at Sherisha Solar plant due to loss of evacuation path. | 1 GD-1 Chattisgarh 03-12-2025 10:55 03-12-2025 11:57 01:02 43 - 0.05% - 84754 70318 Complete outage of 220KV Sherisha S/S: At 10:55 hrs / 03-12-2025, 220 kV Raipur-Sherisha -1 S/C tripped due to mal operation of PLCC (Carrier Channel-2 Failing) at Sherisha end. Generation loss of 43 MW occurred at Sherisha Solar plant due to loss of evacuation path. 1. 220kV Sherisha Raipur line 2. 220/33KV Sherisha ICT-1 | grid_india_gd/grid_events/2025-12-01
G00038 | 2025-12 | 15 | GD-1 | Gujarat | GJ | Western | 2025-12-04T03:56 | 2025-12-04T15:18 | 11.37 | 41 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path generation loss of 19MW occurred. | 2 GD-1 Gujarat 04-12-2025 03:56 04-12-2025 15:18 11:22 41 - 0.07% - 61294 51170 Complete outage of 400 kV Khavda PSS-10 AGEL S/S: At 03:56Hrs/ 04-12-2025, 400KV Khavda PS1-Khavda PSS10 single circuit tripped on overvoltage stage-1 operation due to breaking of B-Phase Jumper wire on tower No-10 at Khavda PSS10. Overvoltage protection also operated and DT sent at KPS end. Due to loss of evacuation path generation loss of 19MW occurred. 1. 400KV Khavda PS1-Khavda PSS10 Ckt-1 | grid_india_gd/grid_events/2025-12-01
G00039 | 2025-12 | 2 | GD-1 | Uttar Pradesh | UP | Northern | 2025-12-04T05:46 | 2025-12-04T10:14 | 4.47 | 0 | 205 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Uttar Pradesh 04-12-2025 05:46 04-12-2025 10:14 04:28 0 205 0.00% 0.41% 35686 49506 i)220/132kV Harduaganj(UP) has double main & transfer bus scheme at 220kV level. ii)As reported, at 05:46 hrs, due to breakdown (blast) of B-Ph CT of Bus coupler, bus bar protection operated at both the buses | 2 GD-1 Uttar Pradesh 04-12-2025 05:46 04-12-2025 10:14 04:28 0 205 0.00% 0.41% 35686 49506 i)220/132kV Harduaganj(UP) has double main & transfer bus scheme at 220kV level. ii)As reported, at 05:46 hrs, due to breakdown (blast) of B-Ph CT of Bus coupler, bus bar protection operated at both the buses of 220kV Harduaganj(UP). iii)This led to tripping of all the elements connected to both 220kV Bus-1 & 2 and complete blackout occurred at 220 kV Harduaganj (UP). iv)As per PMU at Bareilly(PG), B-N phase to earth fault was observed with delayed fault clearing time of 280ms. v)As per SCADA, change in demand of approx 205 MW in UP control area was observed. vi)Substation normalized at 10:14 hrs via charging of 220 kV Haduaganj-Sikandra Rao (UP) Ckt and 220kV Bus-1 at Harduaganj (UP). 1)220 kV Haduaganj-Sikandra Rao (UP) Ckt 2)220 kV Harduaganj-Etah (UP) Ckt 3)220 kV Harduaganj-Khurja (UP) Ckt-1 & 2 4)20 kV Harduaganj-Boner (UP) Ckt 5)220 kV Harduaganj-Atrauli(UP) Ckt 6)220 kV Harduaganj-Jahagirabad (UP) Ckt 7)220 kV Harduaganj-Rukhi (UP) Ckt 8)220 kV Harduaganj-Harduaganj Ext (UP) Ckt-1 & 2 9)220 kV Bus 1 & 2 at Harduaganj (UP) 10)220/132 kV 160 MVA ICT-1 & 2 at Harduaganj(UP) | grid_india_gd/grid_events/2025-12-01
G00040 | 2025-12 | 24 | GD-1 | 400kV TISCO(DVC) |  |  | 2025-12-05T19:21 | 2025-12-05T20:34 | 1.22 | 0 | 94 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 400kV TISCO(DVC) 05-12-2025 19:21 05-12-2025 20:34 01:13 0 94 0.00% 0.43% 31791 21829 400kV TISCO S/s connected through 400kV TISCO Baripada S/C and 400kV TISCO Jamshedpur S/C lines. Prior to the disturbance 400kV TISC- Baripada S/C was under planned shutdown and TISCO draw power radially thr | 1 GD-1 400kV TISCO(DVC) 05-12-2025 19:21 05-12-2025 20:34 01:13 0 94 0.00% 0.43% 31791 21829 400kV TISCO S/s connected through 400kV TISCO Baripada S/C and 400kV TISCO Jamshedpur S/C lines. Prior to the disturbance 400kV TISC- Baripada S/C was under planned shutdown and TISCO draw power radially through Jamshedpur. During charging attempt of Baripada line from TISCO end, Y-Phase LA at Baripada got burst and created Y-Earth fault. Fault was sensed by 400kV Jamshedpur- TISCO and 400kV Baripada-Jamshedpur line in Z-3 protection and after 800 msec both lines got tripped from Jamshedpur and Baripada end respectively. 400kV TISCO S/s became dead, and 95 MW load loss reported at TISCO S/s. 400 kV TISCO- Jamshedpur-S/C 400KV-JAMSHEDPUR-BARIPADA-S/C | grid_india_gd/grid_events/2025-12-01
G00041 | 2025-12 | 3 | GI-1 | Himachal Pradesh | HP | Northern | 2025-12-06T09:49 | 2025-12-06T10:29 | 0.67 | 0 | 160 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GI-1 HP 06-12-2025 09:49 06-12-2025 10:29 00:40 0 160 0.00% 0.24% 52740 65431 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 were carrying 73 MW and 64 MW respectively (as per SCADA). i | 3 GI-1 HP 06-12-2025 09:49 06-12-2025 10:29 00:40 0 160 0.00% 0.24% 52740 65431 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 were carrying 73 MW and 64 MW respectively (as per SCADA). iii)As reported, at 16:24 hrs, 132 KV CT of B-ph Bus coupler bay blasted. During the same time, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 tripped from Salal end (exact nature and location of fault yet to be shared). iv)As per DR at Salal(NH) end, B-N fault converted to R-B-N fault again converted to R-Y-B fault occurred. Fault current was Ir=~2.105kA, Iy=~2.148kA, Ib=~2.036kA from Salal end for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 and Ir=~1.852kA, Iy=~1.951kA, Ib=~1.877kA from Salal end for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-2. Fault sensed in zone-3 at Salal end. Line tripped from Salal end after zone-3 time delay. v)As per PMU at Kishenpur(PG), R-B phase to phase fault converted to 3-phase fault was observed with delayed fault clearing time of 1040ms. vi)As per SCADA, change in demand of approx 180 MW is observed in J&K control area. 1)220 KV Khodri(UK)-Majri(HP) (UK) Ckt-1 2)220 KV Khodri(UK)-Majri(HP) (UK) Ckt-2 3)132 KV Majri-Kala Amb(HP) Ckt | grid_india_gd/grid_events/2025-12-01
G00042 | 2025-12 | 4 | GI-2 | Punjab | PB | Northern | 2025-12-07T14:12 | 2025-12-07T15:29 | 1.28 | 0 | 125 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Punjab 07-12-2025 14:12 07-12-2025 15:29 01:17 0 125 0.00% 0.22% 50440 55618 i)400/220kV Abdullapur(PG) has one & half breaker scheme at 400kV level and 400/220kV Ludhiana(PG) has double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220 KV DandhariKalan(PS)-Ludhia | 4 GI-2 Punjab 07-12-2025 14:12 07-12-2025 15:29 01:17 0 125 0.00% 0.22% 50440 55618 i)400/220kV Abdullapur(PG) has one & half breaker scheme at 400kV level and 400/220kV Ludhiana(PG) has double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 & 2 were carrying ~33 MW & ~29 MW respectively. iii)As reported, at 14:12 hrs, 400 KV Panchkula-Abdullapur (PG) Ckt-2 tripped on R-B phase to phase fault with fault distance of 2.061km and Fault current of 31.24kA from Abdullapur & fault distance of 63km and Fault current of 4.72kA from Panchkula. iv)400 KV Panchkula-Abdullapur (PG) Ckt-1 also tripped during the same time on R-B phase to phase fault due to kite string (exact location and nature of fault yet to be shared). v)Hitachi make relay at Dandharikalana(PS) end of 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 & 2 sensed this fault and 86 Master Trip Relay operated in Out of Zone Disturbance Pickup, as “2 PHASE FAULT DETECTED” Signal was wrongly connected to “86 OPTD” in Relay Logic by default. vi)This led to tripping of both 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 & 2 from Dandharikalan(PS) end only. vii)As per PMU at Ludhiana(PG), R-B double phase fault with fault clearing time of 80ms was observed. viii)As per SCADA, change in demand of approx 125 MW in Punjab control area was observed. ix)As remedial measure, wrong mapping has been corrected and tested in the Relay Logic. 1)400 KV Pa | grid_india_gd/grid_events/2025-12-01
G00043 | 2025-12 | 5 | GI-1 | Delhi | DL | Northern | 2025-12-08T10:44 | 2025-12-08T10:58 | 0.23 | 0 | 285 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GI-1 Delhi 08-12-2025 10:44 08-12-2025 10:58 00:14 0 285 0.00% 0.43% 62715 67012 i)220/66kV Mehrauli(DTL) has double main Bus arrangement at 220kV side. ii)During antecedent condition, 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-2 was under planned shutdown from 10:05 hrs for tree trimming. 220KV | 5 GI-1 Delhi 08-12-2025 10:44 08-12-2025 10:58 00:14 0 285 0.00% 0.43% 62715 67012 i)220/66kV Mehrauli(DTL) has double main Bus arrangement at 220kV side. ii)During antecedent condition, 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-2 was under planned shutdown from 10:05 hrs for tree trimming. 220KV DIAL-Mehrauli (DTL) Ckt-1 & 2 were on no-load. 220kV Bus coupler at Mehrauli(DTL) was in ON position. iii)As reported, at 10:44 hrs, 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 tripped on Y-B phase to phase fault with fault distance of 2.9 km and fault current of Iy=~2.22kA and Ib=~2.26kA from Mehrauli(DV). As per DR, differential protection operated; fault clearing time was ~60 ms. iv)As per PMU at Mandaula(PG), B-N phase to earth fault was observed with fault clearing time of 120 ms. v)As per SCADA, change in demand of approx 285 MW in Delhi control area is observed. vi)As reported, load was normalized by taking 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-2 in service at 10:58 hrs. 1) 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 | grid_india_gd/grid_events/2025-12-01
G00044 | 2025-12 | 16 | GD-1 | Gujarat | GJ | Western | 2025-12-11T01:27 | 2025-12-13T13:20 | 59.88 | 47 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 52.6 MW Occurred at Gadhsisa (Renew Power) Wind Power Plant due to loss of single evacuation path. | 3 GD-1 Gujarat 11-12-2025 01:27 13-12-2025 13:20 59:53 47 - 0.07% - 62810 49521 Complete outage of 220 kV Gadhsisa S/S (Renew Power): At 01:27 hrs / 11-12-2025, 220 kV Bhuj-Gadhsisa-1 S/C (73.3 km, Twin AL-59) tripped on B-E fault, auto recloser unsuccessful at Bhuj End and Auto recloser not operated in Gadhsisa end. During patrolling, it was found that B phase tension insulator got damaged at tower location no. 2. As informed by Renew Power, upper part of tower was damaged due to attempt of conductor theft. Tower at location number 2 is a multi circuit tower having 220 kV Bhuj-Baranda-1 S/C and 220 kV Bhuj-Devsar-1 S/C. Emergency shutdown of above circuits were taken to attend the damaged part of tower. Generation loss of 52.6 MW Occurred at Gadhsisa (Renew Power) Wind Power Plant due to loss of single evacuation path. 1. 220kV Bhuj-Gadhsisa S/C 2. 220kV Gadhsisa Bus-1 3. 220kV Gadhsisa Bus-2 4. 220/33 kV 160MVA Gadhsisa ICT-1 | grid_india_gd/grid_events/2025-12-01
G00045 | 2025-12 | 25 | GD-1 | 220kV RENGALI(Odisha) |  |  | 2025-12-12T19:06 | 2025-12-13T00:04 | 4.97 | 100 | 13 | FALSE | FALSE | FALSE | FALSE | FALSE | Total load loss of 10 MW reported at Rengali S/s and 100 MW generation loss at Rengali HEP. | 2 GD-1 220kV RENGALI(Odisha) 12-12-2025 19:06 13-12-2025 00:04 04:58 100 13 0.31% 0.06% 32286 22775 At 19:06 Hrs on 12.12.2025, Y phase Bus-1 post insulator of 220 kV Bus coupler at Rengali S/s snapped and created Y- Earth bus fault. Fault was sensed in zone -4 protection by all emanating lines and got tripped after 250 msec in Z-4 protection (Bus bar protection not in service), resulting in 220kV Rengali S/s became dead. At the same time Rengali HEP unit -1 & 2 also tripped. Total load loss of 10 MW reported at Rengali S/s and 100 MW generation loss at Rengali HEP. 220KV-Rengali-Rengali (PG)-2 220KV-Rengali-Rengali PH-2 220 kV Rengali-Tarkera 220 kV Rengali-Deogarh Rengali HEP Unit 1 & 2 | grid_india_gd/grid_events/2025-12-01
G00046 | 2025-12 | 17 | GD-1 | Gujarat | GJ | Western | 2025-12-12T22:08 | 2025-12-13T02:20 | 4.2 | 24 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 24 MW occurred at Kotda Madh (WPP) due to loss of evacuation path. | 4 GD-1 Gujarat 12-12-2025 22:08 13-12-2025 02:20 04:12 24 - 0.04% - 66768 55065 Complete outage of 220 kV Kotda Madh (Alfanar) S/S: At 22:08 hrs /12-12-2025, 220 kV Bhuj PS- Kotda Madh single circuit tripped on B-E fault due to falling of other dead line spare conductor . Due to line tripping, 220kV Kotda Madh SS went dark. Generation loss of 24 MW occurred at Kotda Madh (WPP) due to loss of evacuation path. 1. 220kV Bhuj- Kotda Madh (Netra) s/c | grid_india_gd/grid_events/2025-12-01
G00047 | 2025-12 | 18 | GD-1 | Gujarat | GJ | Western | 2025-12-13T03:04 | 2025-12-13T03:43 | 0.65 |  | 168 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of connectivity 400 kV Nicol S/S blacked out leading to generation loss of 168 MW. | 5 GD-1 Gujarat 13-12-2025 03:04 13-12-2025 03:43 00:39 - 168 - 0.33% 61219 51045 Complete outage of 400 kV Nicole S/S (Torrent): At 03:04 Hrs /13-12-2025, 400kV Nicol-Pirana (PG) and 400kV Nicol Vadavi tripped on overvoltage protection maloperation. Due to loss of connectivity 400 kV Nicol S/S blacked out leading to generation loss of 168 MW. Power supply extended to 400kV Nicol by charging 220kV Nicol Khanpur D/C (Normally kept open by SLDC Gujarat). 1. 400kV Nicol-Pirana 2. 400kV Nicol-Vadavi | grid_india_gd/grid_events/2025-12-01
G00048 | 2025-12 | 6 | GD-1 | Punjab | PB | Northern | 2025-12-13T03:55 | 2025-12-13T06:09 | 2.23 | 0 | 28 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 6 GD-1 Punjab 13-12-2025 03:55 13-12-2025 06:09 02:14 0 28 0.00% 0.07% 30259 38557 i)220/66kV Naraingarh(PS) has double main bus scheme at 220kV level. 220 KV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-1 & 2 are on single tower. ii)During antecedent condition, 220 KV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-1 & 2 were carrying ~14 MW each. iii)As reported, at 03:55 hrs, during construction of NHAI highway road, some object came in contact with the conductor of both 220kV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-1 & 2 which were on same tower. iv)As further reported by SLDC Punjab, 220 KV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-1 tripped on R-N phase to earth fault (zone-1) with fault current of 6.983 kA from Naraingarh(PS) (exact location of fault yet to be shared). v)220 KV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-2 also tripped at the same time on 3 phase to earth fault (zone-1) with fault distance of 4.751 km and fault current of Ir=~7.57 kA, Iy=~8.923 kA & Ib=~8.754 kA from Naraingarh(PS). vi)Due to tripping of both 220 KV Amritsar(PG)-Naraingarh(PS) (PSTCL) Ckt-1 & 2, supply to 220/66kV 160 MVA ICT-1 and 100 MVA ICT-2 at Naraingarh(PS) failed and complete blackout occurred at 220/66kV Naraingarh(PS) S/s. vii)As per PMU at Amritsar(PG), two consecutive R-N phase to earth faults followed by B-N phase to earth fault with fault clearing time of 120ms, 440ms (delayed) and 120ms respectively were observed. viii)As per SCADA, change in demand of approx 28 MW in Punjab control area wa | grid_india_gd/grid_events/2025-12-01
G00049 | 2025-12 | 20 | GD-1 | Madhya Pradesh | MP | Western | 2025-12-14T10:28 | 2025-12-14T11:15 | 0.78 |  | 348 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GD-1 Madhya Pradesh 14-12-2025 10:28 14-12-2025 11:15 00:47 - 348 - 0.47% 82576 74371 Complete outage of 220kV Seoni(MP) S/S: At 10:24 hrs / 14-12-2025, 220 kV Seoni(MP)-Seoni(PG)-1 (4.2 km, Single Zebra, 208 MW Thermal Rating (545.87 A)) tripped on Directional Earth Fault(DEF) operation at Seoni( | 7 GD-1 Madhya Pradesh 14-12-2025 10:28 14-12-2025 11:15 00:47 - 348 - 0.47% 82576 74371 Complete outage of 220kV Seoni(MP) S/S: At 10:24 hrs / 14-12-2025, 220 kV Seoni(MP)-Seoni(PG)-1 (4.2 km, Single Zebra, 208 MW Thermal Rating (545.87 A)) tripped on Directional Earth Fault(DEF) operation at Seoni(MP) end and was holding from Seoni(PG) end, the currents observed from Seoni(PG) end DR prior to the incident are IR=491 A, IY=901 A, IB=485 A. As reported from SLDC Madhya Pradesh, line DEF protection due to sparking from isolator misalignment. With the tripping of 220 kV Seoni(MP)-Seoni(PG)-1, all load shifted on 220 kV Seoni(MP)-Seoni(PG)-2 leading to rise in loading to 310 MW resulting in thermal stress in circuit-2. As a result, Y phase isolator Jaw / Post Insulator collapsed on current transformer of 220 kV Seoni(MP)-Seoni(PG)-2 at Seoni(MP) at 10:28 hrs. 220 kV Seoni(MP)-Seoni(PG)-2 tripped on Zone-2 at Seoni(PG) after 440 msec Zone-2 time delay). With this tripping, bus bar protection operated in 220 kV Seoni(MP)-Bus-1 and 220/132 kV Seoni(MP)-ICT-1 (160 MVA) tripped. 220/132 kV Seoni(MP)-ICT-1 (160 MVA) and 220/132 kV Seoni(MP)-ICT-3 (160 MVA) were hand tripped by site at 10:29 hrs. Complete loss of supply occurred at 220 kV Seoni(MP) and entire load was shifted to 132 kV network leading to overloading of 132 kV Chindwara network and tripping multiple lines at 132 kV Chindwara on Load trimming scheme at 10:29 hrs. After 2 minutes at 10:31 hrs, 132 kV Sarni Network overload | grid_india_gd/grid_events/2025-12-01
G00050 | 2025-12 | 7 | GI-1 | Delhi | DL | Northern | 2025-12-15T04:15 | 2025-12-15T04:42 | 0.45 | 0 | 120 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GI-1 Delhi 15-12-2025 04:15 15-12-2025 04:42 00:27 0 120 0.00% 0.32% 29743 37504 i)220/66kV South Wazirabad(DTL) has double main Bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Geeta Colony-South Wazirabad(DV) (DTL) Ckt-1, 220 KV Gopalpur-South Wazirabad(DV) (DTL) Ckt-1, 220 | 7 GI-1 Delhi 15-12-2025 04:15 15-12-2025 04:42 00:27 0 120 0.00% 0.32% 29743 37504 i)220/66kV South Wazirabad(DTL) has double main Bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Geeta Colony-South Wazirabad(DV) (DTL) Ckt-1, 220 KV Gopalpur-South Wazirabad(DV) (DTL) Ckt-1, 220 KV Kashmiri Gate-South Wazirabad(DV) (DTL) Ckt-1, 220 KV Mandola(PG)-South Wazirabad(DV) (DTL) Ckt-1 & 3, 220/66 KV 100 MVA ICT-1 & 160 MVA ICT-2 at South Wazirabad(DTL) were connected to 220 KV Bus -2 at South Wazirabad(DTL). 220kV Bus coupler at South Wazirabad(DTL) was in closed position. iii)As reported, at 04:15 hrs, R-N phase to earth fault occurred on 220 KV Geeta Colony-South Wazirabad(DV) (DTL) Ckt-1 (exact reason, nature and location of fault need to be shared). iv)Due to delayed clearance of the said fault, as per DR, LBB operated and all the elements connected to 220 KV Bus -2 at South Wazirabad(DTL) tripped and Bus-2 became dead (DR was not time synced). v)As per PMU at Mandaula(PG), R-N phase to earth fault was observed with delayed fault clearing time of 200 ms. vi)As per SCADA, change in demand of approx 120 MW in Delhi control area is observed. However, as reported by SLDC Delhi, load loss of 94 MW (Wazirabad: 29 MW, Kashmiri Gate: 12 MW, RPH: 27 MW, Geeta Colony: 11 MW and I.P. Stn: 15 MW) occurred in Delhi control area. 11 no.s of 33kV feeders at I.P. Stn tripped on under frequency relay operation at 04:15 hrs and restored at 05:10 hrs. vii)As reported by SLDC De | grid_india_gd/grid_events/2025-12-01
G00051 | 2025-12 | 8 | GI-2 | Uttar Pradesh | UP | Northern | 2025-12-16T06:34 | 2025-12-16T10:11 | 3.62 | 1250 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GI-2 Uttar Pradesh 16-12-2025 06:34 16-12-2025 10:11 03:37 1250 0 2.78% 0.00% 45018 54835 i)During antecedent condition, both the 660 MW unit-1&2 at Obra C TPS were in service and generating ~617 MW & ~635 MW respectively. ii)As reported, at 06:34 hrs, 765kV Obra_C-Unnao line tripped on Y-N fault. | 8 GI-2 Uttar Pradesh 16-12-2025 06:34 16-12-2025 10:11 03:37 1250 0 2.78% 0.00% 45018 54835 i)During antecedent condition, both the 660 MW unit-1&2 at Obra C TPS were in service and generating ~617 MW & ~635 MW respectively. ii)As reported, at 06:34 hrs, 765kV Obra_C-Unnao line tripped on Y-N fault. As reported, fault distance was ~18.5km from Unnao end and ~328km from Obra_C end. Fault current was ~1.8kA from Obra_C end and 9.5 km from Unnao end. iii)As per PMU at Lucknow(PG) and DR received, Y-N fault which cleared within 100msec is observed. iv)At the same time, 660 MW Unit-1&2 at Obra_C TPS and 765/400kV 1000 MVA ICT-1 at Obra_C (UP) also tripped. As reported, Units and ICT-1 tripped on earth fault protection operation. v)As per SCADA, change in generation of ~1250 MW occurred at Obra C TPS during the event. 1)765 KV Obra_C_TPS-Unnao (UP) Ckt 2)660 MW Unit-1 at Obra_C TPS (UP) 3)660 MW Unit-2 at Obra_C TPS (UP) 4)765/400kV 1000 MVA ICT-1 at Obra_C(UP) | grid_india_gd/grid_events/2025-12-01
G00052 | 2025-12 | 9 | GI-2 | Uttar Pradesh | UP | Northern | 2025-12-16T07:29 | 2025-12-16T10:16 | 2.78 | 780 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-2 Uttar Pradesh 16-12-2025 07:29 16-12-2025 10:16 02:47 780 0 1.61% 0.00% 48474 57091 i)During antecedent condition, both the 600 MW units of Anpara C and 500 MW units of Anpara D were in service and generating 366 MW , 574 MW , 476 MW & 475 MW respectively. MW loading of 400kV Anpara-Obra_B li | 9 GI-2 Uttar Pradesh 16-12-2025 07:29 16-12-2025 10:16 02:47 780 0 1.61% 0.00% 48474 57091 i)During antecedent condition, both the 600 MW units of Anpara C and 500 MW units of Anpara D were in service and generating 366 MW , 574 MW , 476 MW & 475 MW respectively. MW loading of 400kV Anpara-Obra_B line and 400kV Obra_B-Obra_C line were 675 MW (towards Obra_B) and 257 MW (towards Obra_C) respectively. ii)As reported, at 07:29 hrs, 765kV Anpara_C-Unnao line tripped on R-N fault. As reported, fault distance was ~18km from Unnao end and ~357km from Anpara_C end. Fault current was ~2.3kA from Anpara_C end and 6.7km from Unnao end. iii)As per PMU at Lucknow(PG) and DR received, R-N fault which cleared within 100msec with unsuccessful A/R operation due to permanent nature of fault is observed. iv)With the tripping of 765kV Anpara_C-Unnao line, line loading of 400kV Anpara-Obra_B line increased to more than 1100 MW . On this contingency, case-3 of SPS of Anpara complex related to loading of 400kV Anpara-Obra_B line operated. On the operation of SPS, 500 MW Unit-2 at Anpara-D tripped and ~220 MW & ~80 MW generation backdown occurred at Anpara-C & D respectively. 1 unit of Anpara C which was supposed to trip on SPS operation couldn’t trip due to issue in SPS logic communication at Anpara C end. v)As per SCADA, total generation backdown of ~780 MW occurred at Anpara C & D during the event. vi)As reported, Anpara-C shall plan the inspection of SPS trip signal communication issue at their | grid_india_gd/grid_events/2025-12-01
G00053 | 2025-12 | 19 | GI-1 | Maharastra |  |  | 2025-12-16T14:39 | 2025-12-16T14:51 | 0.2 |  | 191 | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GI-1 Maharastra 16-12-2025 14:39 16-12-2025 14:51 00:12 - 191 - 0.27% 82998 70448 Partial outage of 220/66 kV Kharadpada (DNH) S/S: At 14:39 Hrs /16-12-2025, 220/66 kV 160 MVA Kharadpada (DNH) ICT 4 tripped on Differential protection operation due to Y phase LA blast (HV side). With this tripping, | 6 GI-1 Maharastra 16-12-2025 14:39 16-12-2025 14:51 00:12 - 191 - 0.27% 82998 70448 Partial outage of 220/66 kV Kharadpada (DNH) S/S: At 14:39 Hrs /16-12-2025, 220/66 kV 160 MVA Kharadpada (DNH) ICT 4 tripped on Differential protection operation due to Y phase LA blast (HV side). With this tripping, 220/66 kV 160 MVA Kharadpada ICT 1 got overloaded and tripped on Over Current protection operation. As reported by DNH, 66 kV Kharadpada Bus coupler was kept open for load management (220/66 kV 100 MVA ICTs 2&3 connected section remained in service) & part of the load only at 66 kV side got affected (220/66 kV 160 MVA ICTs 1&4 connected section got affected) due to the tripping. Load loss of 191MW (As reported by DNH) occurred due to the event. 1. 220/66 kV 160 MVA Kharadpada ICT 4 2. 220/66 kV 160 MVA Kharadpada ICT 1 | grid_india_gd/grid_events/2025-12-01
G00054 | 2025-12 | 26 | GD-1 | 400kV PVUNL(Jharkhand) |  |  | 2025-12-20T11:23 | 2025-12-20T12:35 | 1.2 | 665 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Total 665 MW generation loss reported at PVUNL due to loss of evacuation path. | 3 GD-1 400kV PVUNL(Jharkhand) 20-12-2025 11:23 20-12-2025 12:35 01:12 665 0 2.22% 0.00% 29925 22933 At 11:06 Hrs on 20/12/2025, 400 kV New Ranchi-Patratu-1 line tripped due to conductor snapped and 400 kV New Ranchi-Patratu-2 was under planned shutdown. After tripping of 400 kV Patratu- New Ranchi-1 Line, 400 kV PVUNL- Tenughat Line tripped on SPS operation. Subsequently, PVUNL generation around 665 MW was evacuated through 400 kV PVUNL-Patratu D/C and 400/220 kV ICTs at Patratu. At 11:23 Hrs, during charging attempt of 400kV Ranchi-Patratu-1 line from Patratu end, faulty line tripped on SOTF and at the same time bus bar/LBB protection operated at 400kV Patratu S/s resulted in 400kV Patratu-PVUNL D/C got tripped. 400kV PVUNL became dead. Total 665 MW generation loss reported at PVUNL due to loss of evacuation path. 400 kV Patratu- New Ranchi -1 400 kV PVUNL- Tenughat 400 kV PVUNL- Patratu-1 400 kV PVUNL- Patratu-2 Elements Tripped Details of Grid Events during the Month of December 2025 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss | grid_india_gd/grid_events/2025-12-01
G00055 | 2025-12 | 21 | GD-1 | Madhya Pradesh | MP | Western | 2025-12-20T19:41 | 2025-12-21T05:15 | 9.57 |  |  | TRUE | FALSE | FALSE | FALSE | TRUE | No generation loss (RE Solar) occurred. | 8 GD-1 Madhya Pradesh 20-12-2025 19:41 21-12-2025 05:15 09:34 - - - - 78043 66486 Complete outage of 220kV Kanwani RE S/S (Masaya Solar): At 19:41 Hrs/20.12.2025, During the scheduled maintenance and relay testing activity on the 33 kV system at 220kV Kanwani(Masaya Solar), transformer protection operated in response to an unintended grounding / abnormal potential condition and consequently led to the tripping of the 220 kV Kanwani ICT along with 220kV-Kanwani- Bhawsinghpura line. 220 KV Kanwani s/s went into dark. No generation loss (RE Solar) occurred. 1. 220kV Bhawsinghpura-Kanwani ckt 2. 220/33kV ICT Kanwani | grid_india_gd/grid_events/2025-12-01
G00056 | 2025-12 | 22 | GD-1 | Maharastra |  |  | 2025-12-23T16:23 | 2025-12-23T18:28 | 2.08 | 11 |  | FALSE | FALSE | FALSE | FALSE | TRUE | As informed by Ghatnandur RE, due to loss of evacuation path generation loss of 11 MW occurred. | 9 GD-1 Maharastra 23-12-2025 16:23 23-12-2025 18:28 02:05 11 - 0.01% - 83832 72806 Complete outage of 220 kV Ghatnandur S/S: At 16:23 Hrs on 23-12-2025, 220kV Kallam– Ghatnandur line tripped due to mal-operation of BCU unit of Bay 208 (TBC) at Kallam SS. As informed by Ghatnandur RE, due to loss of evacuation path generation loss of 11 MW occurred. Line normalized and generation restored at 18:28 Hrs. 1. 220kV Kallam– Ghatnandur TL | grid_india_gd/grid_events/2025-12-01
G00057 | 2025-12 | 10 | GD-1 | HP, Punjab |  |  | 2025-12-24T16:18 | 2025-12-24T18:28 | 2.17 | 175 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | v)As per SCADA, loss of generation of ~175 MW occurred at Pong HEP due to tripping of 66 MW Unit-3, 4 & 5. | 10 GD-1 HP, Punjab 24-12-2025 16:18 24-12-2025 18:28 02:10 175 0 0.33% 0.00% 53592 55150 i)220kV Pong (BBMB) has main & transfer bus scheme. Main bus is divided into two parts (Bus-1A & 1B) through bus sectionaliser. ii)During antecedent condition, 66 MW unit-3, 4 & 5 were running and generating 66 MW , 50 MW & 60 MW respectively. iii)As reported, at 16:18 hrs, bus bar protection operated at 220kV Pong(BBMB) leading to tripping of all the elements connected to 220kV Bus-1A & 1B. During event analysis, it was found that external tripping initiated in 220kV bus coupler however bus coupler CB didn’t open. Due to this, LBB of bus coupler breaker operated leading to tripping of both 220kV Bus-1A & B. During investigation, broken cables have been found in trip circuit of bus coupler breaker. Further review is being done. iv)As per PMU at Jalandhar(PG), no fault in system in observed. v)As per SCADA, loss of generation of ~175 MW occurred at Pong HEP due to tripping of 66 MW Unit-3, 4 & 5. 1)220KV Bus 1 & 2 at Pong(BB) 2)220 KV Jalandhar-Pong (BB) Ckt-1 & 2 3)220 KV Bairasiul(NH)-Pong(BB) (PG) Ckt-1 4)220 KV Jessore(HP)-Pong(BB) (PG) Ckt-1 5)220 KV Pong(BB)-Dasuya(PS) (BBMB) Ckt-1 & 2 6)66 MW Pong HPS - UNIT 3 , 4, 5 | grid_india_gd/grid_events/2025-12-01
G00058 | 2025-12 | 11 | GD-1 | Rajasthan | RJ | Northern | 2025-12-26T10:46 | 2025-12-26T12:13 | 1.45 | 270 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per PMU plot of MW of Nokhra(IP), solar generation loss of ~270 MW occurred at Nokhra Restation. | 11 GD-1 Rajasthan 26-12-2025 10:46 26-12-2025 12:13 01:27 270 0 0.43% 0.00% 62345 72291 i)Generation of 220kV Nokhra (IP) stations evacuates through 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt. ii)During antecedent condition, 220kV Nokhra (IP) was generating approx 270 MW (as per PMU). iii)As reported, at 10:46hrs, 220/33 kV 100 MVA ICT-2 tripped on differential protection operation on B-N fault. iv)At the same time, 220kV Bhadla2-Nokhra line also tripped. Reason of the tripping is yet to be received. v)As per PMU at Bhadla2(PG), B-N phase to earth fault cleared within 100 msec is observed. vi)As per PMU plot of MW of Nokhra(IP), solar generation loss of ~270 MW occurred at Nokhra Restation. 1) 220/33kV 100 MVA ICT-2 at Nokhra(IP) 2) 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt | grid_india_gd/grid_events/2025-12-01
G00059 | 2025-12 | 12 | GD-1 | Delhi | DL | Northern | 2025-12-29T10:39 | 2025-12-29T10:59 | 0.33 | 0 | 160 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GD-1 Delhi 29-12-2025 10:39 29-12-2025 10:59 00:20 0 160 0.00% 0.23% 60420 70945 i)220/66kV South Wazirabad(DTL) has double main Bus arrangement at 220kV side. ii)As reported, at 10:39hrs, during bus shifting operation of 66/11kV 20 MVA transformer, bus fault occurred at 66kV bus. On this fault, | 12 GD-1 Delhi 29-12-2025 10:39 29-12-2025 10:59 00:20 0 160 0.00% 0.23% 60420 70945 i)220/66kV South Wazirabad(DTL) has double main Bus arrangement at 220kV side. ii)As reported, at 10:39hrs, during bus shifting operation of 66/11kV 20 MVA transformer, bus fault occurred at 66kV bus. On this fault, all four 220/66kV ICTs at 220kV South Wazirabad(DTL) tripped on overcurrent earth fault protection operation. iii)As per PMU at Manolda(PG), R-Y-B three phase fault with delayed clearance of ~600 msec is observed. v)As per SCADA, change in demand of ~200 MW in Delhi control area is observed. However, as reported by SLDC Delhi load loss of ~160 MW occurred in Delhi control area. 1)220/66 KV 100 MVA ICT-1 & 3 at South Wazirabad(DTL) 2)220/66 KV 160 MVA ICT-2 & 4 at South Wazirabad(DTL) | grid_india_gd/grid_events/2025-12-01
G00060 | 2025-12 | 13 | GD-1 | Rajasthan | RJ | Northern | 2025-12-29T16:12 | 2025-12-29T19:12 | 3 | 0 | 260 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Neemrana(PG)-Kushkhera(RS) (RS) Ckt-1 2) 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 13 GD-1 Rajasthan 29-12-2025 16:12 29-12-2025 19:12 03:00 0 260 0.00% 0.44% 54531 59343 i)220kV Kushkhera(RS) has double main bus scheme. ii)During antecedent condition,220kV 220 KV Neemrana(PG)-Kushkhera(RS) (RS) Ckt-1 and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt-1 were carrying 108 MW & 186 MW respectively. iii)As reported, at 16:12hrs, bus post B-ph jumper of 220 KV Neemrana(PG)-Kushkhera(RS) (RS) Ckt-1(connected at 220kV Bus-II) at Khuskhera end damaged and created bus fault. On this fault, bus bar protection of 220kV Bus-2 at Kushkhera(RS) operated leading to tripping of all the elements connected at 220kV Bus-II. iv)As per PMU at Neemrana(PG), B-N phase to earth fault cleared within 100 msec is observed. v)As per SCADA, change in demand of ~260 MW in Rajasthan control area is observed. 1) 220 KV Neemrana(PG)-Kushkhera(RS) (RS) Ckt-1 2) 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2025-12-01
G00061 | 2025-12 | 23 | GI-1 | Maharastra |  |  | 2025-12-29T22:19 | 2025-12-30T00:27 | 2.13 | 137 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 137 MW & no load loss occurred due to the event. | 10 GI-1 Maharastra 29-12-2025 22:19 30-12-2025 00:27 02:08 137 - 0.21% - 66759 56889 Partial outage of 220 kV Paras S/S (220 kV Paras Thermal Power station Maharashtra): At 22:19 Hrs/29-12-2025, 220 kV Paras Main Bus 2 and all the connected elements tripped on LBB operation of 220 kV Balapur ckt 3. 220 kV Paras- Balapur 3, 220 kV Paras- Akola 2, 220 kV Paras- Chikhali 2, 220 kV Paras- Malkapur, 220/7.5 kV 50 MVA Paras ST-2, 250 MW Paras Unit 3 & 220 kV Paras Bus coupler tripped during the event. As seen from PMU plot, there was no fault signature during the tripping and the LBB tripping seems to be a mal-operation. After isolating 220 kV Balapur ckt 3, all the elements were restored at 220 kV Paras. Generation loss of 137 MW & no load loss occurred due to the event. 1. 220 kV Paras- Balapur 3 2. 220 kV Paras- Akola 2 3. 220 kV Paras- Chikhali 2 4. 220 kV Paras- Malkapur 5. 220 kV Paras Bus coupler 6. 220/7.5 kV 50 MVA Paras ST-2 7. 250 MW Paras Unit 3 Elements Tripped Details of Grid Events during the Month of December 2025 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 t | grid_india_gd/grid_events/2025-12-01
G00062 | 2026-01 | 1 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-01-01T17:24 | 2026-01-01T17:45 | 0.35 | 0 | 278 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-1 Jammu and Kashmir 01-01-2026 17:24 01-01-2026 17:45 00:21 0 278 0.00% 0.48% 48934 57617 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) | 1 GI-1 Jammu and Kashmir 01-01-2026 17:24 01-01-2026 17:45 00:21 0 278 0.00% 0.48% 48934 57617 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying 150 MW each) was feeding Ziankote load. 220kV Wagoora-Ziankote(JK) D/C (one ckt LILO at Budgam) (carrying 253 MW and 206 MW) were connected at other bus and feeding Alusteng, Drass, Kargil, Khalsti and Leh S/s. As reported by SLDC-J&K, 220 KV Ziankote – Alusteng (JKPDD) D/C were carrying 139 MW each. iii)As reported, at 17:24 hrs, 220 KV Ziankote – Alusteng (JKPDD) Ckt-1 tripped on R-N phase to earth fault with fault distance of 34.99 km and fault current of 3.4 kA from Ziankote(JK); zone-1 distance protection operated at Ziankote end. Fault occurred due to a vulture sitting on tower no. 156 of 220 KV Ziankote – Alusteng (JKPDD) Ckt-1. iv)At the same time, 220 KV Ziankote – Alusteng (JKPDD) Ckt-2 also tripped due to over-loading from Ziankote end. v)As per PMU at Kishenpur(PG), R-N phase to earth fault is observed with delayed fault clearing time of 200ms. vi)As per SCADA, change in demand of approx 278MW is observed in J&K control area. 1) 220 KV Ziankote – Alusteng (JKPDD) Ckt-1 2) 220 KV Ziankote – Alusteng (JKPDD) Ckt-2 | grid_india_gd/grid_events/2026-01-01
G00063 | 2026-01 | 23 | GD-1 | Madhya Pradesh | MP | Western | 2026-01-02T13:17 | 2026-01-02T14:29 | 1.2 |  | 278 | FALSE | TRUE | FALSE | FALSE | TRUE | 1 GD-1 Madhya Pradesh 02-01-2026 13:17 02-01-2026 14:29 01:12 - 278 - 0.39% 83537 71195 Complete outage of 220kV Rajgarh (MP) S/S: At 13:17 hrs / 02-01-2026, B phase tension disc insulator string of 220 kV Rajgarh(MP)-Bus-2 (Double main bus configuration) failed, resulting in bus bar protection operation in 220 kV Rajgarh(MP)-Bus-2 and all connected elements {220 kV Rajgarh(PG)-Rajgarh(MP)-2, 220 | 1 GD-1 Madhya Pradesh 02-01-2026 13:17 02-01-2026 14:29 01:12 - 278 - 0.39% 83537 71195 Complete outage of 220kV Rajgarh (MP) S/S: At 13:17 hrs / 02-01-2026, B phase tension disc insulator string of 220 kV Rajgarh(MP)-Bus-2 (Double main bus configuration) failed, resulting in bus bar protection operation in 220 kV Rajgarh(MP)-Bus-2 and all connected elements {220 kV Rajgarh(PG)-Rajgarh(MP)-2, 220 kV Rajgarh(MP)-Clean Wind-1, 220/132 kV Rajgarh(MP)-ICT-1 (160 MVA) and 220/132 kV Rajgarh(MP)-ICT-2 (160 MVA)} tripped. After 2 seconds, 220 kV Rajgarh(MP)-Rajgarh(PG)-1 tripped on distance protection from Rajgarh(MP) end leading to loss of connection from grid. 220/132 kV Rajgarh(MP)-ICT-3 (160 MVA) was handtripped by site due to loss of supply from grid. Supply failure of 220/132 kV Rajgarh(MP) resulted in overloading of 132 kV downstream network and blackout of 132 kV Rajgarh(MP), 132 kV Jhabua, 132 kV Meghnagarand 132 kV Petlawar. Load loss of 278 MW occurred at 220 kV Rajgarh(MP) and downstream network. 1. 220 kV Rajgarh- Rajgarh(MP) 1 2. 220 kV Rajgarh- Rajgarh(MP) 2 3. 220 kV Rajgarh(MP)- Clean Wind 4. 220/132 kV 160 MVA Rajgarh(MP) ICT 1 5. 220/132 kV 160 MVA Rajgarh(MP) ICT 2 6. 220/132 kV 160 MVA Rajgarh(MP) ICT 3 | grid_india_gd/grid_events/2026-01-01
G00064 | 2026-01 | 2 | GD-1 | Himachal Pradesh | HP | Northern | 2026-01-02T13:38 | 2026-01-02T13:54 | 0.27 | 250 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | v)As per SCADA, generation loss of approx 250 MW occurred at Bhakra Left HEP . | 2 GD-1 Himachal Pradesh 02-01-2026 13:38 02-01-2026 13:54 00:16 250 0 0.46% 0.00% 54800 61687 i)During antecedent condition, 126 MW Unit-2 &3 at Bhakra Left(BB) were running and generating approx 125 MW each. ii)As reported, at 13:38 hrs, CB A-13 of 126 MW Unit-3 at Bhakra Left(BB) was opened on full load during load throw off test conducted in the presence of maintenance agencies. iii)During this time, LBB operated due to damaged burnt coil of Y phase limb of CB A-13 which further resulted in tripping of all the elements connected to 220kV Bhakra Left(BB). iv)As per PMU at Bhakra Right(BB), Y-N phase to earth fault was observed with delayed fault clearing time of 440 ms. v)As per SCADA, generation loss of approx 250 MW occurred at Bhakra Left HEP . 1) 220 KV Bhakra_L-Ganguwal (BB) Ckt-1 2) 220 KV Bhakra_L-Ganguwal (BB) Ckt-2 3) 220 KV Bhakra_L-Ganguwal (BB) Ckt-3 4) 220/66kV 150 MVA ICT-1 Bhakra Left(BB) 5) 126 MW Unit-2 at Bhakra Left(BB) 6) 126 MW Unit-3 at Bhakra Left(BB) 7) 66 KV Bhakra_L(BB)-NFL Ckt-3 8) 66 KV Bhakra_L(BB)-Rakkar Ckt | grid_india_gd/grid_events/2026-01-01
G00065 | 2026-01 | 24 | GI-1 | Madhya Pradesh | MP | Western | 2026-01-03T04:39 | 2026-01-03T08:34 | 3.92 |  | 50 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GI-1 Madhya Pradesh 03-01-2026 04:39 03-01-2026 08:34 03:55 - 50 - 0.10% 61892 51433 Complete outage of 220kV Bhanpura S/S: 220 KV Bhanpura - Nipaniya and Bhanpura -Suwasra lines both are on same tower. 220 KV Bhanpura Suwasra line was already under breakdown since 2:10 Hrs/ 03.01.2026 and dischar | 2 GI-1 Madhya Pradesh 03-01-2026 04:39 03-01-2026 08:34 03:55 - 50 - 0.10% 61892 51433 Complete outage of 220kV Bhanpura S/S: 220 KV Bhanpura - Nipaniya and Bhanpura -Suwasra lines both are on same tower. 220 KV Bhanpura Suwasra line was already under breakdown since 2:10 Hrs/ 03.01.2026 and discharge rod was connected on P1 (towards CB) side of CT at Bhanpura station. 220 kV Bhanpura- Ranpur & 220 KV Bhanpura – Nipaniya were also under outage since 04:19 Hrs/03.01.2026 & 02:10 Hrs/03.01.2026 hrs respectively. When test charge was taken of 220 KV Bhanpura Nipaniya line from Nipaniya 220kV Substation end at 4:39hrs/03.01.2026, due to fault, flash-over occurred and arcing current flowed in Suwasra line and entered from P2 to P1 terminal (of CT at Bhanpura end) and after P1 grounded through connected discharge rod. Current flowed towards P2 to P1, created fault in bus bar zone and as a result Busbar protection operated. Same current also appeared in Distance Protection relay (R~394A, Y~504A, B~565A) during bus bar tripping operation. As 220 kV Bhanpura s/s is having Single Main Bus & Transfer Bus scheme, all the elements at 220 kV level tripped at 220/132 kV Bhanpura substation. 220 kV Bhanpura- Modak & 220/132 kV 160 MVA Bhanpura ICT 1 also tripped during the event. As reported by MP SLDC, 132 kV side of Bhanpura was intact so no load loss was occurred. 1. 220 kV Bhanpura- Suwasra 2. 220 kV Bhanpura- Nipaniya 3. 220 kV Bhanpura- Ranpur 4. 220 kV Bhanpura- Modak 5. 220/132 kV 16 | grid_india_gd/grid_events/2026-01-01
G00066 | 2026-01 | 3 | GD-1 | Rajasthan | RJ | Northern | 2026-01-04T07:02 | 2026-01-04T07:15 | 0.22 | 0 | 124 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GD-1 Rajasthan 04-01-2026 07:02 04-01-2026 07:15 00:13 0 124 0.00% 0.23 % 43552 53102 i)220/132kV Debari(RS) has double main and transfer bus scheme at 220kV level. ii)As reported, at 06:04 hrs, 220 KV Debari(RS)-RAPS_A(NP) (RS) Ckt tripped on Y-N phase to earth fault with fault distance of 103.8 | 3 GD-1 Rajasthan 04-01-2026 07:02 04-01-2026 07:15 00:13 0 124 0.00% 0.23 % 43552 53102 i)220/132kV Debari(RS) has double main and transfer bus scheme at 220kV level. ii)As reported, at 06:04 hrs, 220 KV Debari(RS)-RAPS_A(NP) (RS) Ckt tripped on Y-N phase to earth fault with fault distance of 103.8 km and fault current of 1.02 kA from Debari(RS) end and fault distance of 97.18 km and fault current of 1.835 kA from RAPS_A(NP) end. iii)As further reported, at 07:02 hrs, during charging aƩempt of 220 KV Debari(RS)-RAPS_A(NP) (RS) Ckt, bus bar protection mal-operated at 220kV Debari(RS) which resulted in tripping of all 220/132kV ICTs also. Complete blackout occurred at 220/132kV Debari(RS). iv)Supply to following area were disturbed during this event: a)132 KV GSS Dakankotra w.e.f. 07:02 to 07:45 hrs (43 mins) (Along with railway Feeder at Dakan Kotra) b)132 KV GSS Bhatewar w.e.f. 07:02 to 08:18 hrs (16mins) c)132 KV GSS Mavli w.e.f. 07:02 to 07:27 hrs (25 mins) (Along with railway Feeder at Mavli(29min)) d)132 KV HZL feeder and 132 KV UCW feeder and Local w.e.f. 07:02 to 07:42hrs (40 mins) feeders v)As per PMU at RAPP_C(NP), no fault was observed in the system. vi)As per SCADA change in demand of approx 124 MW in Rajasthan control area was observed. vii)Supply was taken from 220 kV Debari-Amberi (PG) Ckt at 07:15hrs. 220 KV Debari(RS)-RAPS_A(NP) (RS) Ckt was charged after replacement of disc string fail at TL- 306 (Y Phase). 1) 220 KV Debari(RS)-RAPS_A(NP) (RS) Ckt 2) 220 KV De | grid_india_gd/grid_events/2026-01-01
G00067 | 2026-01 | 25 | GD-1 | Gujarat | GJ | Western | 2026-01-05T19:12 | 2026-01-06T00:05 | 4.88 | 109 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 109 MW occurred due to loss of evacuation path. | 3 GD-1 Gujarat 05-01-2026 19:12 06-01-2026 00:05 04:53 109 - 0.14% - 75340 69508 Complete outage of 220kV Gadhsisa S/S(Renew):At 19:12 hrs on 05-01-2026, the 220 kV Bhuj–Gadhsisa line tripped due to a B-phase to ground fault. During line patrolling, a conductive foreign object was found hanging between Tower No. 6/1 and 6/0. The line trip caused bus bar protection to operate, and the DT sent from the Gadhsisa end to Bhuj resulted in the tripping of both ICTs. Generation loss of 109 MW occurred due to loss of evacuation path. 1. 220kV Bhuj-Gadhsisa S/C 2. 220kV Gadhsisa Bus-1 3. 220kV Gadhsisa Bus-2 4. 220/33 kV 160MVA Gadhsisa ICT-1 | grid_india_gd/grid_events/2026-01-01
G00068 | 2026-01 | 26 | GD-1 | Gujarat | GJ | Western | 2026-01-06T18:04 | 2026-01-06T19:44 | 1.67 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 53.1 MW Occurred at Manza (Powerica) due to loss of evacuation path. | 4 GD-1 Gujarat 06-01-2026 18:04 06-01-2026 19:44 01:40 - - - - 77282 72013 Complete outage of 220kV Manja S/S(Powerica): At 18:04 hrs / 06-01-2026, Busbar protection operated during the first time charging of 220/33 kV Manza-ICT-2, resulting in black out of 220 kV Manza substation due to loss of evacuation path. On inspection it was found that a shorting link was inadvertently left installed in Current Transformer Junction Box (CTJB) of the new 220/33 kV Manza-ICT-2 bay (204 Bay). This shorting in CTJB was done during installation phase because the CT secondary could not be connected to the bus bar protection relay immediately because the adjacent Bays (202 & 203) were live and to protect the open CT secondary circuits from developing dangerous high voltages. When the system was made ready for FTC, the shorting link was removed from the Control & Relay Panel (CRP) but missed in the outdoor field CTJB due to human error. When Bay204 was energized, primary current flowed through the CTs. However, because of the shorting link in the CTJB, the secondary current circulated locally within the box and did not reach the REB670 Busbar protection relay, creating a differential current mimicking an internal bus fault. The 220 kV Manza-Bus-1 tripped on bus bar protection operation and 220 kV Manza substation became dead. Generation loss of 53.1 MW Occurred at Manza (Powerica) due to loss of evacuation path. 1. 220 Jamkhambaliya – Manja line 2. 220/33 KV ICT-1 3. 220/33 KV ICT-2 4. 220 kV | grid_india_gd/grid_events/2026-01-01
G00069 | 2026-01 | 4 | GI-2 | Uttar Pradesh | UP | Northern | 2026-01-07T16:47 | 2026-01-07T18:06 | 1.32 | 0 | 53 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Uttar Pradesh 07-01-2026 16:47 07-01-2026 18:06 01:19 0 53 0.00% 0 .09% 49380 57685 i)16:47:53:320 hrs: Jack bus fell on 400kV Bus-1 & 2 creating R-Y-B-N three phase to earth bus faut. ii)400kV Bus-II was under shutdown and bus bar protection of 400kV Bus-I didn’t operate on three phase bus f | 4 GI-2 Uttar Pradesh 07-01-2026 16:47 07-01-2026 18:06 01:19 0 53 0.00% 0 .09% 49380 57685 i)16:47:53:320 hrs: Jack bus fell on 400kV Bus-1 & 2 creating R-Y-B-N three phase to earth bus faut. ii)400kV Bus-II was under shutdown and bus bar protection of 400kV Bus-I didn’t operate on three phase bus fault on 400kV Bus-I. iii)All the lines and ICTs at Kanpur(PG) sensed the fault in Z-4 and remote end sensed the fault in Z-2. iv)All the 400kV elements except i.e., 400kV Agra line, Allahabad line-II, Ballabhgarh line-I, II & III, Auraiya line-I&II, and ICT-I & II tripped in Z-4 distance protection operation. v)400kV Kanpur-Kanpur765 D/C neither sense fault in Z-4 at Kanpur(PG) end nor in Z-2 from Kanpur765 end. vi)By 16:47:54 hrs, all the lines except 400kV Kanpur-Kanpur765 D/C tripped. vii)Further at 16:47:54:880 hrs, 400kV Kanpur-kanpur1 D/C and 400kV Kanpur-Lucknow D/C tripped on Z-3 distance protection operation. 400kV Kanpur-kanpur1 D/C should have tripped in Z-2, distance protection setting of the D/C shall be reviewed (As informed, LSR impedance hasn’t been considered in Z-2 line protection). 1)220 KV Kanpur(PG)-Rania(UP) (PG) Ckt-1 2)400 KV Kanpur_GIS-Kanpur (PG) Ckt-1 3)400 KV Kanpur_GIS-Kanpur (PG) Ckt-2 4)400KV Bus 1 at Kanpur(PG) 5)400 KV Kanpur(PG)-Auraiya(NT) (PG) Ckt-1 6)400 KV Kanpur(PG)-Auraiya(NT) (PG) Ckt-2 7)400/220 kV 315 MVA ICT 1 at Kanpur(PG) 8)400/220 kV 315 MVA ICT 2 at Kanpur(PG) 9)400 KV Kanpur-Agra (PG) Ckt-1 10)400 KV Allahabad-Kanpur (PG) Ckt-1 11)40 | grid_india_gd/grid_events/2026-01-01
G00070 | 2026-01 | 40 | GI-1 | Kerala | KL | Southern | 2026-01-07T18:58 | 2026-01-07T21:19 | 2.35 | 0 | 280 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GI-1 KERALA 07-01-2026 18:58 07-01-2026 21:19 02:21 0 280 0.00% 0.01% 48 639.91 49570.55 Tripping of 220kV Bus-1 at Madakathara of KSEB In the antecedent condition 220KV-MADAKATHARA-CHALAKUDY-1 line and 220kV Bus Section 2A were under planned shutdown due to retrofitting works. As per the reports | 8 GI-1 KERALA 07-01-2026 18:58 07-01-2026 21:19 02:21 0 280 0.00% 0.01% 48 639.91 49570.55 Tripping of 220kV Bus-1 at Madakathara of KSEB In the antecedent condition 220KV-MADAKATHARA-CHALAKUDY-1 line and 220kV Bus Section 2A were under planned shutdown due to retrofitting works. As per the reports submitted, during the returning of the shutdown, 220 kV bus isolator (227) connected to 220KV-MADAKATHARA-CHALAKUDY-1 line to Bus Section 1A where in the bus dropper accidentally came into contact with an earth rod leading to B-G bus fault in the Bus Section 1A. BBP protection operated and tripped both the Bus Section 1A and Bus Section 1B. This led to the Tripping of 220kV Bus-1 at Madakathara of KSEB. 400KV/220KV MADAKKATHARA-ICT-1, 400KV/220KV MADAKKATHARA-ICT-2, 400KV/220KV MADAKKATHARA- ICT-3, 220KV-ELAPULLY-MADAKATHARA-1, 220KV-LOWER PERIYAR-MADAKATHARA-1 | grid_india_gd/grid_events/2026-01-01
G00071 | 2026-01 | 27 | GD-1 | Gujarat | GJ | Western | 2026-01-07T19:06 | 2026-01-07T20:47 | 1.68 | 100 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 103.5 MW occurred due to loss of evacuation. | 5 GD-1 Gujarat 07-01-2026 19:06 07-01-2026 20:47 01:41 100 - 0.13% - 78080 69266 Complete outage of 220kV Gadhsisa S/S(Renew): At 19:06 Hrs/ 07-01-2026, 220kV Bhuj–Gadhsisa line tripped due to B phase to ground fault without A/R attempt. Unintended Bus bar protection operated at Gadhsisa end and DT received at Bhuj end. Generation loss of 103.5 MW occurred due to loss of evacuation. 1 220kV Bhuj-Gadhsisa S/C 2 220kV Gadhsisa Bus-1 3 220kV Gadhsisa Bus-2 4 220/33 kV 160MVA Gadhsisa ICT-1 | grid_india_gd/grid_events/2026-01-01
G00072 | 2026-01 | 5 | GI-2 | Uttar Pradesh | UP | Northern | 2026-01-08T08:01 | 2026-01-08T09:19 | 1.3 | 1375 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | ix)As per SCADA, generation loss of approx 1375 MW occured at Anpara TPS(UP). | 5 GI-2 Uttar Pradesh 08-01-2026 08:01 08-01-2026 09:19 01:18 1375 0 2.59 % 0.00% 53132 62237 i)400/132kV Anpara(UP) S/s have double main and transfer bus arrangement at 400kV level and double main bus arrangement at 132kV level. ii)During antecedent condition, 132kV Anpara-Morwa Ckt was under shutdown and 132kV Bus coupler was in ON position. 210 MW UNIT 1, 2 & 3 and 500 MW UNIT 4 & 5 at Anpara TPS were in running condition and were generating approx 187 MW, 176 MW, 153 MW, 392 MW and 466 MW respectively (as per SCADA). iii)As informed by SLDC UP , 132kV CWTF11 and CWTF22 were supplying power to Cooling water pumps for 210 MW Anpara TPS - UNIT 1, 2 & 3 and 132kV CWTF33 was supplying power to Cooling water pumps for 500 MW Anpara TPS - UNIT 4 & 5. Similarly, 132kV STNX11 and STNX22 were supplying auxiliary power to 210 MW Anpara TPS - UNIT 1, 2 & 3 and 132kV STNX33 and STNX44 were supplying auxiliary power to 500 MW Anpara TPS - UNIT 4 & 5. iv)As reported, at 08:01 hrs, Y-ph LA of 132kV Bus-A at Anpara TPS blasted causing fault in 132kV Bus-A at Anpara TPS. Bus bar protection of 132kV did not operated on this fault due to non-operation of check zone relay. v)Due to this, 132KV Anpara-Rihand (UP) Ckt-1 & 2, 132KV Anpara(UP)-Bina Ckt and all other 132 kV elements (station transformes supplying auxiliaries and CWTF supplying cooling water pumps) connected to Bus-A and B tripped on over-current earth fault protection operation and both the 132kV buses at Anpara TPS became dead. vi | grid_india_gd/grid_events/2026-01-01
G00073 | 2026-01 | 28 | GI-2 | Madhya Pradesh | MP | Western | 2026-01-09T04:21 | 2026-01-09T07:57 | 3.6 | 302 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GI-2 Madhya Pradesh 09-01-2026 04:21 09-01-2026 07:57 03:36 302 - 0.46% - 65838 52114 Partial Outage of 400kV Vindyachal S/S: At 04:21 hrs/09.01.2026 VSTPS Stage-1 400KV Bus-1 tripped at due to suspected malfunction of the output auxiliary relay (RXMS1). Due to relay malfunction, bus-bar protectio | 6 GI-2 Madhya Pradesh 09-01-2026 04:21 09-01-2026 07:57 03:36 302 - 0.46% - 65838 52114 Partial Outage of 400kV Vindyachal S/S: At 04:21 hrs/09.01.2026 VSTPS Stage-1 400KV Bus-1 tripped at due to suspected malfunction of the output auxiliary relay (RXMS1). Due to relay malfunction, bus-bar protection operated. Following elements also tripped due to tripping of Bus-1 at same time. 1. VINDHYACHAL - 400KV - BUS 1 2. 400 kV SASAN - VINDHYACHAL(PS) - I 3. 400 kV VINDHYACHAL - HVDC - I 4. VSTPS I - UNIT 3 5. VSTPS I - UNIT 5 6. VINDHYACHAL HVDC POLE - II | grid_india_gd/grid_events/2026-01-01
G00074 | 2026-01 | 41 | GI-1 | TAMILNADU |  |  | 2026-01-10T20:57 | 2026-01-10T22:09 | 1.2 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-1 TAMILNADU 10-01-2026 20:57 10-01-2026 22:09 01:12 0 0 0.00% 0.00% 4 2258.39 43136.62 Tripping of 230kV Bus-1 and 2 at KAYATHAR of TANTRANSCO In the antecedent condition, all the elements are connected to 230kV Bus-1 at Kayathar. As per the reports submitted, the triggering incident was Y phas | 9 GI-1 TAMILNADU 10-01-2026 20:57 10-01-2026 22:09 01:12 0 0 0.00% 0.00% 4 2258.39 43136.62 Tripping of 230kV Bus-1 and 2 at KAYATHAR of TANTRANSCO In the antecedent condition, all the elements are connected to 230kV Bus-1 at Kayathar. As per the reports submitted, the triggering incident was Y phase jumper cut in between bus selection disconnector (89A & 89B) in 230kV Chekkanurunni feeder and creating a bus fault leading to Bus Bar protection operation and tripping of all the elements connected to Bus-1 at Kayathar end. This led to the tripping of 230kV Bus-1 and 2 at KAYATHAR of TANTRANSCO 230KV-Chekkanurani-KAYATHAR(TN)-1, 230KV- KAYATHAR(TN)-KAYATHAR-1, 230KV-KAYATHAR(TN)- KAYATHAR-2, 230KV-KAYATHAR(TN)-KINNIMANGLAM-2, 230KV-KAYATHAR(TN)-SANGANERI-1, 230KV- KAYATHAR(TN)-TIRUNELVELI-1, 230KV-KAYATHAR(TN)-TTPS- 1, 230KV-KAYATHAR(TN)-TTPS-2, 230KV-KAYATHAR(TN)- TTPS-AUTO-1, 230KV-KAYATHAR(TN)-UDAYATHOOR-1, 230KV-KAYATHAR(TN)-VEERANAM-1 | grid_india_gd/grid_events/2026-01-01
G00075 | 2026-01 | 42 | GI-2 | Telangana | TG | Southern | 2026-01-11T06:48 | 2026-01-11T09:30 | 2.7 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-2 TELANGANA 11-01-2026 06:48 11-01-2026 09:30 02:42 0 0 0.00% 0.00% 3 7609.77 46813.16 Tripping of 400kV Bus-2 of Shankarpally of TGTRANSCO The triggering incident was failure of R-ph breaker at Shankarapally end connected to 400kV Bus-2, while hand tripping 125MVAR bus reactor creating a bus | 10 GI-2 TELANGANA 11-01-2026 06:48 11-01-2026 09:30 02:42 0 0 0.00% 0.00% 3 7609.77 46813.16 Tripping of 400kV Bus-2 of Shankarpally of TGTRANSCO The triggering incident was failure of R-ph breaker at Shankarapally end connected to 400kV Bus-2, while hand tripping 125MVAR bus reactor creating a bus fault and bus bar protection operated tripping all the breakers (main) connected to 400kV Bus-2 tripped. This led to the tripping of 400kV Bus-2 at Shankarapally SHANKARAPALLY - 400KV - Bus 2 | grid_india_gd/grid_events/2026-01-01
G00076 | 2026-01 | 6 | GD-1 | Rajasthan | RJ | Northern | 2026-01-11T10:36 | 2026-01-11T14:25 | 3.82 | 264 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | v)As per PMU, solar generation loss of approx 264 MW was observed at AHEJ3L(IP). | 6 GD-1 Rajasthan 11-01-2026 10:36 11-01-2026 14:25 03:49 264 0 0.46% 0.00 % 56782 71110 i)Generation of 220kV AHEJ3L(IP) station evacuates through 220KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt-1. ii)During antecedent condition, 220kV AHEJ3L(IP) station was generating approx 264 MW (as per SCADA). iii)As reported, at 10:36 hrs, 220 KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt-1 tripped on Y-N phase to earth fault with fault current of 1.08kA from AHEJ3L end (exact nature, location and reason of fault yet to be shared) which led to complete blackout out of 220kV AHEJ3L(IP) S/s. iv)As per PMU at Fatehgarh2(PG), Y-N phase to earth fault was observed with fault clearing time of 80ms. Voltage dipped upto 0.943 pu during fault. v)As per PMU, solar generation loss of approx 264 MW was observed at AHEJ3L(IP). 1) 220 KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt Details of Grid Events during the Month of January 2026 in Nort hern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss ( | grid_india_gd/grid_events/2026-01-01
G00077 | 2026-01 | 29 | GI-2 | Gujarat | GJ | Western | 2026-01-11T11:47 | 2026-01-11T14:00 | 2.22 | 721 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 721 MW occurred due to the event. | 7 GI-2 Gujarat 11-01-2026 11:47 11-01-2026 14:00 02:13 721 - 0.82% - 88129 75000 Partial Outage of 400/33kV NTPC Khavda PSS2 S/S:At 11:47 Hrs/11-01-2026, 400/33 kV NTPC PSS2 ICT 2 tripped on Over current protection operation (three phase fault observed in PMU). At the same time, 404 Main bay of 400/33 kV NTPC PSS2 ICT 3 tripped on Oil Surge relay operation. Due to these above mentioned trippings & 408 Bay under forced outage, 400/33 kV NTPC PSS2 ICTs 4 , 5 & 400 kV NTPC PSS2 Bus 2 became dead. Generation loss of 721 MW occurred due to the event. 1. 400 kV NTPC PSS2 Bus 2 2. 400/33 kV NTPC PSS2 ICT 2 3. 400/33 kV NTPC PSS2 ICT 3 4. 400/33 kV NTPC PSS2 ICT 4 5. 400/33 kV NTPC PSS2 ICT 5 | grid_india_gd/grid_events/2026-01-01
G00078 | 2026-01 | 7 | GD-1 | Haryana | HR | Northern | 2026-01-11T14:37 | 2026-01-11T15:48 | 1.18 | 0 | 325 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GD-1 Haryana 11-01-2026 14:37 11-01-2026 15:48 01:11 0 325 0.00% 0.56% 5 5340 57579 i)400/220KV Gurgaon(PG) and 220/66/33KV Gurgaon sec72 has double main bus system in 220KV side. 220kV Sec72 Gurgaon(HR) has source from 400/220kV Gurgaon(PG) station through three (03) 220kV feeders and 220kV Sec72 | 7 GD-1 Haryana 11-01-2026 14:37 11-01-2026 15:48 01:11 0 325 0.00% 0.56% 5 5340 57579 i)400/220KV Gurgaon(PG) and 220/66/33KV Gurgaon sec72 has double main bus system in 220KV side. 220kV Sec72 Gurgaon(HR) has source from 400/220kV Gurgaon(PG) station through three (03) 220kV feeders and 220kV Sec72 Gurgaon-Sec69 Gurgaon ckt. ii)As reported, at 14:37 hrs, 220 KV Sohna Road-Sec69 Gurgaon ckt tripped on B-N fault. Fault was in Z-1 from Sohna Road end and in Z-2 from Sec69 Gurgaon end. On this fault, line instantaneously tripped from Sohna Road how ever due to issue in PLCC carrier communication, line tripped with the delay of ~400 msec from Sec69 Gurgaon end. During this delayed clearance of fault, 220kV Sec72 Gurgaon-Sec69 Gurgaon ckt tripped from Sec72 Gurgaon end in back up earth fault protection and 220 KV Gurgaon(PG)- Sec72 Gurgaon(HV)(HVPNL)-1,2&3 tripped from Gurgaon(PG) end in high set earth fault protection. iii)As per PMU at Gurgaon(PG), B-N phase to earth fault with delayed clearance of ~400msec is observed. iv)As per SCADA, change in demand of approx ~325MW in Haryana control area is observed. v)As informed by HVPNL, PLCC is healthy in 220 KV Sohna Road-Sec69 Gurgaon ckt however, PLCC carrier communication in 220 KV Sohna Road-Sec69 Gurgaon ckt is configured in only B-ph. As there was B-N fault, it is suspected that carrier signal got disturbed and communication didn’t occur. Necessary review of PLCC scheme is being done to avoid such event in future. 1) 220 KV Sohn | grid_india_gd/grid_events/2026-01-01
G00079 | 2026-01 | 30 | GD-1 | Gujarat | GJ | Western | 2026-01-11T19:03 | 2026-01-11T22:43 | 3.67 | 132 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 137 MW occurred due to the loss of evacuation path. | 8 GD-1 Gujarat 11-01-2026 19:03 11-01-2026 22:43 03:40 132 - 0.17% - 76850 66740 Complete Outage of 220 kV Baranda S/S (Avikiran): At 19:03 hrs/ 11-01-2026, the 220 kV Baranda–Bhuj S/C line tripped due to B-E fault from Baranda end only. Generation loss of 137 MW occurred due to the loss of evacuation path. Auto-reclosure was unsuccessful at the Baranda end while auto-reclosure was successful at the Bhuj end. 1. 220 kV Bhuj-Baranda Elements Tripped Details of Grid Events during the Month of January 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of January 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the | grid_india_gd/grid_events/2026-01-01
G00080 | 2026-01 | 8 | GD-1 | Uttar Pradesh | UP | Northern | 2026-01-13T05:16 | 2026-01-13T06:50 | 1.57 | 50 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 50 MW occurred at Vishnuprayag HEP . | 8 GD-1 Uttar Pradesh 13-01-2026 05:16 13-01-2026 06:50 01:34 50 0 0.15% 0 .00% 34190 46366 i)400/220 kV Muzaffarnagar(UP) S/s have double main and transfer bus arrangement at both 400kV & 220kV level. Generation of Alaknanda HEP and Vishnuprayag HEP also evacuates through Muzaffarnagar(UP) via 400kV Alaknand a-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line. ii)During antecedent condition, 400kV Alaknanda-Vishnuprayag line was under shutdown. Line loading of 400kV Alaknanda-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line were 120 MW & 50 MW respectively. 110 MW unit-2 at Vishnuprayag HEP was running and generating ~50 MW. iii)As reported, at 05:16 hrs, flashover occurred on 400kV R-ph bus post insulator of 400/220 kV ICT-2 at Muzaffarnagar(UP) (connected at 400kV Bus-II). On this fault, bus bar protection of 400kV Bus-II operated leading to tripping of all the elements connected to 400kV Bus-II i.e., 400 KV Meerut(PG)-Muzaffarnagar(UP) (PG) Ckt-1, 400/220 kV 315 MVA ICT 2 & 3 at Muzaffarnagar(UP) and 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt-1. iv)Due to tripping of 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt-1, 110 MW Unit-2 at Vishnuprayag HEP (generating ~50 MW) tripped due to loss of evacuation path. v)As per PMU at Meerut(PG), R-N phase to earth fault which cleared within 100 msec is observed. vi)As per SCADA, generation loss of approx 50 MW occurred at Vishnuprayag HEP . vii)As reported by SLDC UP , no load loss was observed in | grid_india_gd/grid_events/2026-01-01
G00081 | 2026-01 | 9 | GD-1 | Uttar Pradesh | UP | Northern | 2026-01-13T07:43 | 2026-01-13T08:51 | 1.13 | 62 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 62 MW occurred at Vishnuprayag HEP . | 9 GD-1 Uttar Pradesh 13-01-2026 07:43 13-01-2026 08:51 01:08 62 0 0.12% 0 .00% 53160 59369 i)400/220 kV Muzaffarnagar(UP) S/s have double main and transfer bus arrangement at both 400kV & 220kV level. Generation of Alaknanda HEP and Vishnuprayag HEP also evacuates through Muzaffarnagar(UP) via 400kV Alaknand a-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line. ii)During antecedent condition, 400kV Alaknanda-Vishnuprayag line, 400/220 kV 315 MVA ICT 2 at Muzaffarnagar(UP) were under shutdown. Line loading of 400kV Alaknanda-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line were 159 MW & 62 MW respectively. 110 MW unit-4 at Vishnuprayag HEP was running and generating ~62 MW. iii)As reported, at 07:43 hrs, flashover occurred on 400kV Y-ph bus post (bus-II) insulator of transfer bus coupler. On this fault, bus bar protection of 400kV Bus-II operated leading to tripping of all the elements connected to 400kV Bus-II i.e., 400 KV Meerut(PG)-Muzaffarnagar(UP) (PG) Ckt-1, 400/220 kV 315 MVA ICT 3 at Muzaffarnagar(UP) and 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt-1. iv)Due to tripping of 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt-1, 110 MW Unit-4 at Vishnuprayag HEP (generating ~62 MW) tripped due to loss of evacuation path. v)As per PMU at Meerut(PG), Y-N phase to earth fault which cleared within 100 msec is observed. vi)As per SCADA, generation loss of approx 62 MW occurred at Vishnuprayag HEP . vii)As reported by SLDC UP , no load loss was obse | grid_india_gd/grid_events/2026-01-01
G00082 | 2026-01 | 10 | GD-1 | Rajasthan | RJ | Northern | 2026-01-14T13:38 | 2026-01-14T14:31 | 0.88 | 2281 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | iv)As per SCADA, total drop of approx 1680 MW NR RE generation observed during the event. | 10 GD-1 Rajasthan 14-01-2026 13:38 14-01-2026 14:31 00:53 2281 0 4.00% 0.0 0% 56972 63353 i)As reported, at 13:38 hrs, 400kV Bassi-Phagi ckt-2 tripped on R-Y fault. Fault occurred due to kite thread. As per PMU plot of phase current of line at Bassi(PG), R-Y fault which cleared within 100 msec is observed. ii)On this fault during voltage dip, significant dip in RE generation observed which further led to the overvoltage in transmission network. iii)Due to this overvoltage, 765 KV Bhadla2-Fatehgarh2 ckt-3 tripped on overvoltage stage-1. As per PMU plot of phase voltage of line at Fatehgarh2(PG), overvoltage upto Vph:469kV, ~1.06 pu is observed. At the same time, 220 KV Fatehgarh_III(PG)-RSAPL(RENEW SURYA AAYAN PRIVATE LIMITED) Ckt also tripped on overvoltage and RAPS-D unit-1 tripped due to turbine trip during grid disturbance. (Exact reason of RAPS-D unit tripping is yet to be received). Tripping of 220kV RSAPL RE station on overvoltage needs to be reviewed. iv)As per SCADA, total drop of approx 1680 MW NR RE generation observed during the event. Out of which ~300 MW lost due to tripping of RSAPL RE station and ~100 MW at APTFL, ~90 MW at Devikot, ~50 MW at AHEJ4L, ~85 MW at TPGEL, ~180 MW ASEJ2L, ~82 MW at ARTPL and ~135 MW at MSUPL affected due to suspected LVRT/HVRT non-compliance during the event. Additionally, loss of ~600 MW nuclear generation observed at RAPS-D due to tripping of RAPS-D unit-1. 1) 400 KV Bassi(PG)-Phagi(RS) (PG) Ckt-1 2) 765 KV Bhadla_2 (PG)- Fatehgarh | grid_india_gd/grid_events/2026-01-01
G00083 | 2026-01 | 11 | GD-1 | Rajasthan | RJ | Northern | 2026-01-14T14:05 | 2026-01-14T15:43 | 1.63 | 3787 | 252 | TRUE | FALSE | FALSE | FALSE | TRUE | iv)As per SCADA, total drop of approx 3787 MW NR RE generation observed during the event. | 11 GD-1 Rajasthan 14-01-2026 14:05 14-01-2026 15:43 01:38 3787 252 6.95% 0 .41% 54462 61700 i)As reported, at 14:05 hrs, 765kV Sikar2-Aligarh ckt-1 tripped on R-Y-B three phase fault. Fault occurred due to kite thread. As per PMU plot of phase current of line at Sikar2(PG), R-Y-B three phase fault which cleared within 100 msec is observed. ii)On this fault during voltage dip, significant dip in RE generation observed which further led to the overvoltage in transmission network. iii)Due to this overvoltage, 765kV Fatehgarh2-Bhadla2 ckt-1 & 4, 765kV Bikaner-Bhadla2 ckt-1, 765kV Bhadla2-Ajmer ckt-1, 765kV Bhiwani-Narela ckt, 400kV Fatehgarh1-ACME Pool ckt, 400kV Bikaner(PG)-Bikaner Renew Solar ckt, 400kV Bikaner Renew Solar-Renew Surya Ravi ckt and 220kV Bikaner2(PG)-Renew Dinkar ckt tripped tripped on overvoltage stage-1. As per PMU plot of phase voltage of line, Vph: 475kV (1.075 pu) at Bhadla2(PG) and 467kV (1.057 pu) at Bhiwani(PG) is observed. Tripping of 220kV Renew Dinkar RE station on overvoltage needs to be reviewed. iv)As per SCADA, total drop of approx 3787 MW NR RE generation observed during the event. Out of which ~1650 MW lost due to tripping of ACME pooling station, Bikaner Renew Solar, Renew Surya Ravi and Renew Dinkar RE station and ~50 MW at SB Energy, ~66 MW at AHEJ3L, ~74 MW at AHEJ1L, ~35 MW at EDEN, ~135 MW RSUPL, ~88 MW at Avada SSTN, ~78 MW at TPGEL, ~65 MW at Kolayat, ~225 MW ABCRL, ~293 MW at NTPC Nokhra, ~125 MW at Karniser NHPC, ~82 MW at ARTPL and ~6 | grid_india_gd/grid_events/2026-01-01
G00084 | 2026-01 | 12 | GI-2 | Rajasthan | RJ | Northern | 2026-01-14T14:09 | 2026-01-14T23:33 | 9.4 | 925 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | iii)On this fault during voltage dip, as per SCADA, total drop of approx 925 MW NR RE generation observed. | 12 GI-2 Rajasthan 14-01-2026 14:09 14-01-2026 23:33 09:24 925 0 1.73% 0.00 % 53570 60875 i)As reported, at 14:09 hrs, 765kV Sikar2-Aligarh ckt-2 tripped on R-Y fault. Fault occurred due to kite thread. ii) As per PMU plot of phase current of line at Sikar2(PG), R-Y fault which cleared within 100 msec is observed. iii)On this fault during voltage dip, as per SCADA, total drop of approx 925 MW NR RE generation observed. 1) 765 KV Sikar_2(PSTL)-Aligarh(PG) (PASTL) Ckt-2 | grid_india_gd/grid_events/2026-01-01
G00085 | 2026-01 | 43 | GI-1 | Karnataka | KA | Southern | 2026-01-15T11:11 | 2026-01-15T11:18 | 0.12 | 0 | 160 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-1 KARNATAKA 15-01-2026 11:11 15-01-2026 11:18 00:07 0 160 0.00% 0.00 % 54036.98 55391.62 Tripping of Bus-2 of Adakanahalli SS of KPTCL The triggering incident is the BBP maloperation at Adakanahalli SS leading to the tripping of all elements connected to Bus-2 of Adakanahalli SS. This led to t | 11 GI-1 KARNATAKA 15-01-2026 11:11 15-01-2026 11:18 00:07 0 160 0.00% 0.00 % 54036.98 55391.62 Tripping of Bus-2 of Adakanahalli SS of KPTCL The triggering incident is the BBP maloperation at Adakanahalli SS leading to the tripping of all elements connected to Bus-2 of Adakanahalli SS. This led to the Tripping of Bus-2 of Adakanahalli SS of KPTCL. 220KV-BEGUR-ADAKANAHALLI-2, 220KV-KADAKOLA- ADAKANAHALLI-2 | grid_india_gd/grid_events/2026-01-01
G00086 | 2026-01 | 13 | GD-1 | Himachal Pradesh | HP | Northern | 2026-01-15T17:30 | 2026-01-15T19:38 | 2.13 | 294 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, loss of generation of ~294 MW occurred at Pong HEP due to tripping of 66 MW Unit-1, 3, 4, 5 & 6 1)220KV Bus 1 at Pong(BB) 2)220KV Bus 2 at Pong(BB) 3)220 KV Jalandhar-Pong (BB) Ckt-1 4)220 KV Jalandhar-Pong (BB) Ckt-2 5)220 KV Bairasiul(NH)- Pong(BB) (PG) Ckt-1 6)220 KV Jessore(HP)- Pong(BB) (PG) Ckt-1 7)220 KV Pong(BB)- Dasuya(PS) (BBMB) Ckt-1 8)220 KV Pong(BB)-Dasuya(PS) (BBMB) | 13 GD-1 Himachal Pradesh 15-01-2026 17:30 15-01-2026 19:38 02:08 294 0 0.59% 0.00% 49590 59993 i)220kV Pong (BBMB) has main & transfer bus scheme. Main bus is divided into two parts (Bus-1A & 1B) through bus sectionaliser. ii)During antecedent condition, 66 MW unit-1, 3, 4, 5 & 6 were running and generating total ~294 MW . iii)As reported, at 17:30 hrs, 220kV Bus-1A & 1B at Pong(BBMB) tripped due to bus bar protection of both 220kV Bus-1&2. (Exact reason of bus bar protection operation not received yet). iv)Due to tripping of both the 220kV Bus, all the connected 220kV lines along with 66 MW unit-1, 3, 4, 5 & 6 tripped. v)As per PMU at Jalandhar(PG), no fault in system is observed. vi)As per SCADA, loss of generation of ~294 MW occurred at Pong HEP due to tripping of 66 MW Unit-1, 3, 4, 5 & 6 1)220KV Bus 1 at Pong(BB) 2)220KV Bus 2 at Pong(BB) 3)220 KV Jalandhar-Pong (BB) Ckt-1 4)220 KV Jalandhar-Pong (BB) Ckt-2 5)220 KV Bairasiul(NH)- Pong(BB) (PG) Ckt-1 6)220 KV Jessore(HP)- Pong(BB) (PG) Ckt-1 7)220 KV Pong(BB)- Dasuya(PS) (BBMB) Ckt-1 8)220 KV Pong(BB)-Dasuya(PS) (BBMB) Ckt-2 9)66 MW Pong HPS - UNIT 1 10)66 MW Pong HPS - UNIT 3 11)66 MW Pong HPS - UNIT 4 12)66 MW Pong HPS - UNIT 5 13)66 MW Pong HPS - UNIT 6 | grid_india_gd/grid_events/2026-01-01
G00087 | 2026-01 | 15 | GD-1 | Uttar Pradesh | UP | Northern | 2026-01-17T02:08 | 2026-01-17T03:58 | 1.83 | 124 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 50 MW at Vishnuprayag HEP and 74 MW at Alaknanda HEP is observed. | 15 GD-1 Uttar Pradesh 17-01-2026 02:08 17-01-2026 03:58 01:50 124 0 0.38% 0.00% 32726 42303 i)400/220 kV Muzaffarnagar(UP) S/s have double main and transfer bus arrangement at both 400kV & 220kV level. Generation of Alaknanda HEP and Vishnuprayag HEP also evacuates through Muzaffarnagar(UP) via 400kV Alaknand a-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line. ii)During antecedent condition, 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) line was under shutdown. Line loading of 400kV Alaknanda-Muzaffarnagar line was ~18 MW. Generation of Alaknanda HEP and Vishnuprayag HEP wa s evacuating through 400kV Alaknanda-Shrinagar(UK) D/C and 400k V Alaknanda- Muzaffarnagar line. 82.5 MW Unit-4 at Alaknanda HEP and 110 MW unit-2 at Vishnuprayag HEP was running and generating 74 MW & 50 MW respectively. iii)As reported, at 02:08 hrs, flashover occurred on 400kV B-ph bus post insulator of 400/220kV 315 MVA ICT-III at Muzaffarnagar(UP). On this fault, bus bar protection of both 400kV Bus-I & II operated, leading to tripping of all the 400kV elements at Muzaffarnagar(UP). iv)With the tripping of 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt-1, 110 MW Unit-2 at Vishnuprayag HEP (generating ~50 MW) and 82.4 MW Unit-4 at Alaknanda HEP (generating ~74 MW) tripped on overfrequency prot ection due to load generation mismatch. v)As per PMU at Meerut(PG), B-N phase to earth fault which cleared within 100 msec is observed. vi)As per SCADA, generation loss of approx 50 MW at Vishnupra | grid_india_gd/grid_events/2026-01-01
G00088 | 2026-01 | 14 | GD-1 | Punjab | PB | Northern | 2026-01-17T05:11 | 2026-01-17T07:35 | 2.4 | 0 | 138 | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GD-1 Punjab 17-01-2026 05:11 17-01-2026 07:35 02:24 0 138 0.00% 0.29% 36 130 46876 i)220kV DandhariKalanI(PS) Abdullapur(PG) has single bus scheme at 220kV level and double bus scheme at 66kV level. ii)During antecedent condition, 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 & 2 were carry | 14 GD-1 Punjab 17-01-2026 05:11 17-01-2026 07:35 02:24 0 138 0.00% 0.29% 36 130 46876 i)220kV DandhariKalanI(PS) Abdullapur(PG) has single bus scheme at 220kV level and double bus scheme at 66kV level. ii)During antecedent condition, 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 & 2 were carrying ~21 MW & ~19 MW respectively. iii)As reported, at 05:11 hrs, B-ph CT of HV side of 220/66kV Transformer T-1 at DandhariKalan burst. On this fault, 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) D/C and 220 KV Jamalpur(BB)-DandhariKalanI(PS) (PSTCL) Ckt-2 tripped on Z-4 distance protection operation. iv)As per PMU at Ludhiana(PG), two successive B-N fault with delayed clearance of ~240msec during 2nd instance is observed. v)As per SCADA, change in demand of approx 138 MW in Punjab control area was observed. 1) 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-1 2) 220 KV DandhariKalan(PS)-Ludhiana(PG) (PSTCL) Ckt-2 3) 220 KV Jamalpur(BB)-DandhariKalanI(PS) (PSTCL) Ckt-2 | grid_india_gd/grid_events/2026-01-01
G00089 | 2026-01 | 16 | GI-2 | Uttar Pradesh | UP | Northern | 2026-01-17T05:23 | 2026-01-17T09:32 | 4.15 | 84 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 84 MW at Alaknanda HEP is observed. | 16 GI-2 Uttar Pradesh 17-01-2026 05:23 17-01-2026 09:32 04:09 84 0 0.23% 0 .00% 36587 48239 i)400/220 kV Muzaffarnagar(UP) S/s have double main and transfer bus arrangement at both 400kV & 220kV level. Generation of Alaknanda HEP and Vishnuprayag HEP also evacuates through Muzaffarnagar(UP) via 400kV Alaknanda-Muzaffarnagar line and 400kV Vishnuprayag-Muzaffarnagar line. ii)During antecedent condition, only 400 KV Bus-1 along with 400 KV Meerut(PG)-Muzaffarnagar(UP) (PG) Ckt-1, 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt-1 and 400/220 kV 315 MVA ICT 2 & 500 MVA ICT-4 at Muzaffarnagar(UP) were in service. Rest of the 400kV elements were under forced outage since 02:08 hrs tripping incident. 400k V Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) line was under shutdo wn. Line loading of 400kV Alaknanda-Muzaffarnagar line was ~26 MW. Generation of Al aknanda HEP was evacuating through 400kV Alaknanda-Shrinagar(UK ) D/C and 400kV Alaknanda-Muzaffarnagar line. 82.5 MW Unit-4 a t Alaknanda HEP was running and generating 84 MW. iii)As reported, at 05:23 hrs, flashover occurred on 400kV Y-ph bus post insulator of 400kV Alaknanda-Muzaffarnagar line at Muzaffarnagar(UP). On this fault, bus bar protection of both 400kV Bus-I operated, leading to tripping of all the elements connected at 400kV Bus-I at Muzaff arnagar(UP). iv)With the tripping of 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt-1, 82.4 MW Unit-4 at Alaknanda HEP (generating ~84 MW) tripped on over frequency due to load gener | grid_india_gd/grid_events/2026-01-01
G00090 | 2026-01 | 31 | GD-1 | Madhya Pradesh | MP | Western | 2026-01-17T11:41 | 2026-01-17T12:33 | 0.87 | 262 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Solar RE generation loss of 265 MW (U6-81.27 MW & U7-180.93MW) occurred due to loss of evacuation path. | 9 GD-1 Madhya Pradesh 17-01-2026 11:41 17-01-2026 12:33 00:52 262 - 0.30% - 87355 76882 Complete Outage of 220kV Shajapur Unit 6&7 S/S: At 11:41 Hrs/17-01-2026, during an auto-reclose attempt on Y-N fault, 220kV Pachora-Dehripal line tripped from Dehripal end & line was holding at Pachora end. Due to tripping of this line, Shajapur U7 (Dheripal) & Shajapur U6 (Burley, radially connected with Dehripal became dark. Solar RE generation loss of 265 MW (U6-81.27 MW & U7-180.93MW) occurred due to loss of evacuation path. 1. 220kV Pachora- Dehripal 2. 220kV Dehripal-Burley 3. 220KV/33KV SHAJAPUR Unit-7(Dehripal)-ICT-1 4. 220KV/33KV SHAJAPUR Unit-7(Dehripal)-ICT-2 5. 220KV/33KV SHAJAPUR Unit-6(Burley)-ICT-1 | grid_india_gd/grid_events/2026-01-01
G00091 | 2026-01 | 32 | GI-2 | DDDNH UT |  |  | 2026-01-19T00:46 | 2026-01-19T04:47 | 4.02 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-2 DDDNH UT 19-01-2026 00:46 19-01-2026 04:47 04:01 - -- - 62107 51555 Partial Outage of 400 kV Kala S/S: At 00:46/19-01-2026, The 400 kV BUS-1 at KALA GIS tripped during anti theft charging of 400 kV Kala-New Navsari-1 at Kala end through bay 411 due to R phase differential protection operatio | 10 GI-2 DDDNH UT 19-01-2026 00:46 19-01-2026 04:47 04:01 - -- - 62107 51555 Partial Outage of 400 kV Kala S/S: At 00:46/19-01-2026, The 400 kV BUS-1 at KALA GIS tripped during anti theft charging of 400 kV Kala-New Navsari-1 at Kala end through bay 411 due to R phase differential protection operation in BUSBAR MAIN-2 (P741 CUB). 400 kV Kala-New Navsari-1 tripped on SOTF(Y-PH Fault) at the same time. After the analysis of the BUSBAR Relay CUB DR it was reported by POWERGRID WR-2, that the tripping was initiated by R phase differential current, which was due to open neutral core from relay panel to LCC (core continuity not found). No load loss reported in DDDNH area due to the tripping. 1. 400 kV KALA - VAPI - II 2. 400 kV KALA - KUDUS(MSETCL) - I 3. KALA - 400KV - BUS 1 4. KALA 315MVA ICT-1 5. KALA 315MVA ICT-2 | grid_india_gd/grid_events/2026-01-01
G00092 | 2026-01 | 33 | GD-1 | Madhya Pradesh | MP | Western | 2026-01-20T09:02 | 2026-01-20T12:53 | 3.85 | 100 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 100MW occurred at Kanwani due to loss of evacuation path. | 11 GD-1 Madhya Pradesh 20-01-2026 09:02 20-01-2026 12:53 03:51 100 - 0.12% - 86285 78934 Complete Outage of 220 kV Kanwani (Masaya Solar)S/S: At 09:02 hrs on 20-01-2026, the Kanwani–Bhawsingpura line tripped on a B-phase earth fault due to burning of the SF₆ breaker top pad clamp, caused by failure of the ICTs B-phase conductor between the SF₆ breaker top pad clamp and the CT terminal. Generation loss of 100MW occurred at Kanwani due to loss of evacuation path. 1. 220kV Kanwani - Bhawsinghpura Ckt2. 220/33kV ICT at Kanwani | grid_india_gd/grid_events/2026-01-01
G00093 | 2026-01 | 34 | GD-1 | Gujarat | GJ | Western | 2026-01-20T23:45 | 2026-01-21T02:34 | 2.82 | 1 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 1 MW occurred at Srijan Morjar (Continuum Energy) Wind Power Plant due to loss of evacuation path. | 12 GD-1 Gujarat 20-01-2026 23:45 21-01-2026 02:34 02:49 1 - 0.00% - 66643 55215 Complete Outage of 220 kV Srijan Morjar Wind RE S/S :At 23:45 hrs/20.01.2026, the 220 kV Bhuj II-Srijan Morjar-1 S/C tripped due to B-phase to earth fault. Test charging attempt was taken at 02:34 hrs on 21.01.2026 but the line tripped on SOTF (Switch-On-To-Fault) protection. On patrolling damaged B phase suspension insulator was found at Tower location AP20. Generation loss of 1 MW occurred at Srijan Morjar (Continuum Energy) Wind Power Plant due to loss of evacuation path. 1. 220kV Srijan Morjar – Bhuj-II Ckt-1 | grid_india_gd/grid_events/2026-01-01
G00094 | 2026-01 | 17 | GI-2 | Jammu and Kashmir | JK | Northern | 2026-01-21T13:17 | 2026-01-22T14:10 | 24.88 | 0 | 200 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 400kV New Wanpoh-Wagoora (PG) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of January 2026 in Nort hern Region Elements Tripped Sl No. | 17 GI-2 Jammu and Kashmir 21-01-2026 13:17 22-01-2026 14:10 00:53 0 200 0.00% 0.34% 57047 59075 i)400/220kV New Wanpoh(PG) has one and half breaker scheme at 400kV level and 400/220kV Wagoora(PG) S/s has double main and transfer bus scheme at 400kV level. ii)During antecedent condition, 400kV New Wanpoh-Wagoora (PG) Ckt-2 was carrying approx 700 MW from New Wanpoh(PG) to Wagoora(PG). 400kV New Wanpoh-Wagoora (PG) Ckt-1 was under shut down since 11:41 hrs. iii)As reported, at 13:17 hrs, 400kV New Wanpoh-Wagoora (PG) Ckt-2 tripped on Y-B phase to phase fault with fault distance of 6.66 km and fault current of Iy=~7.4 kA and Ib=~6.6 kA from New Wanpoh(PG). iv)As per PMU at New Wanpoh(PG), Y-B phase to phase fault is observed with fault clearing time of 80ms. v)As per SCADA, change in demand of approx 200 MW is observed in J&K control area. 1) 400kV New Wanpoh-Wagoora (PG) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of January 2026 in Nort hern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of th | grid_india_gd/grid_events/2026-01-01
G00095 | 2026-01 | 18 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-01-22T21:25 | 2026-01-22T22:40 | 1.25 | 0 | 245 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GD-1 Jammu and Kashmir 22-01-2026 21:25 22-01-2026 22:40 01:15 0 245 0.00% 0.46% 39678 52694 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) | 18 GD-1 Jammu and Kashmir 22-01-2026 21:25 22-01-2026 22:40 01:15 0 245 0.00% 0.46% 39678 52694 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~130 MW each) was feeding Ziankote load. 220kV Wagoora(PG)-Ziankote(JK) D/C (carrying ~155 MW each) were connected at other bus and feeding Alusteng, Drass, Kargil, Khalsti and Leh S/s. iii)As reported, at 21:25 hrs, 220 KV Wagoora(PG)-Ziankote(JK) (PDD JK) Ckt-1 tripped on R-N phase to earth fault with fault distance of 24km and fault current of 5kA from Wagoora(PG) end and fault distance of 14.24km and fault current of 3.289kA from Ziankote(JK) end. iv)During the same time, 220 KV Wagoora(PG)-Ziankote(JK) (PDD JK) Ckt-2 also tripped sensing the same fault from Wagoora(PG) end only (exact reason and nature of protection operation yet to be shared). v)Due to tripping of 220 KV Wagoora(PG)-Ziankote(JK) (PDD JK) Ckt-1 & 2, supply to Alusteng, Drass, Kargil, Khalsti and Leh S/s failed and complete blackout occurred at 220/66kV Alusteng(JK), Drass(PG), Kargil(PG), Khalsti(PG) and Leh(PG). vi)As per PMU at New Wanpoh(PG), R-N phase to earth fault is observed with fault clearing time of 80ms. vii)As per SCADA, change in demand of approx 245MW is observed in J&K control area. 1) 220 KV Wagoora(PG)-Ziankote(JK) (PDD JK) Ckt-1 2) 220 KV Wagoora(PG)-Ziankote(JK) (PDD JK) Ckt-2 | grid_india_gd/grid_events/2026-01-01
G00096 | 2026-01 | 19 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-01-22T21:41 | 2026-01-22T23:04 | 1.38 | 0 | 215 | FALSE | FALSE | FALSE | FALSE | FALSE | 19 GD-1 Jammu and Kashmir 22-01-2026 21:41 22-01-2026 23:04 01:23 0 215 0.00% 0.42% 38649 50961 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) | 19 GD-1 Jammu and Kashmir 22-01-2026 21:41 22-01-2026 23:04 01:23 0 215 0.00% 0.42% 38649 50961 i)220/132kV Ziankote S/s have two bus at 220kV side i.e., main bus & reserve bus. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~75 MW each) was feeding Ziankote load. 220kV Wagoora(PG)-Ziankote(JK) D/C and 220 KV Ziankote – Alusteng (JKPDD) D/C were already in tripped condition since 21:25hrs. iii)As reported, at 21:41 hrs, 220 KV Amargarh(INDIGRID)-Ziankote(JK) (PDD JK) Ckt-1 & 2 tripped due to operation of master-trip relay without any other relay indication. iv)Due to tripping of 220 KV Amargarh(INDIGRID)-Ziankote(JK) (PDD JK) Ckt-1 & 2, supply to 220kV Ziankote(JK) failed and complete blackout occurred at 220/132kV Ziankote(JK). v)As per PMU at Amargarh(PG), no fault is observed in the system. vi)As per SCADA, change in demand of approx 215MW is observed in J&K control area. 1) 220 KV Amargarh(INDIGRID)-Ziankote(JK) (PDD JK) Ckt-1 2) 220 KV Amargarh(INDIGRID)-Ziankote(JK) (PDD JK) Ckt-2 | grid_india_gd/grid_events/2026-01-01
G00097 | 2026-01 | 20 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-01-23T12:43 | 2026-01-23T17:55 | 5.2 | 84 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 20 GD-1 Jammu and Kashmir 23-01-2026 12:43 23-01-2026 17:55 05:12 84 0 0.15% 0.00% 56233 50986 i)400/220kV Amargarh(INDIGRID S/s has one and half breaker scheme at 400kV level. ii)During antecedent condition, 400 KV Uri_1(NH)-Amargarh (INDIGRID) (INDIGRID) Ckt-2 and 400 KV Uri_2(NH)-Wagoora(PG) (PG) | 20 GD-1 Jammu and Kashmir 23-01-2026 12:43 23-01-2026 17:55 05:12 84 0 0.15% 0.00% 56233 50986 i)400/220kV Amargarh(INDIGRID S/s has one and half breaker scheme at 400kV level. ii)During antecedent condition, 400 KV Uri_1(NH)-Amargarh (INDIGRID) (INDIGRID) Ckt-2 and 400 KV Uri_2(NH)-Wagoora(PG) (PG) Ckt were already under tripped condition. Total generation of Uri-I&II(NH) was evacuating through 400 KV Uri_1(NH)-Amargarh (INDIGRID) (INDIGRID) Ckt-1 only. 120 MW Uri-I HPS - UNIT 3 and 60 MW Uri-II HPS - UNIT 1 & 4 were only in running condition and w ere generating approx 9 MW, 40 MW and 35 MW respectively (as reported by NHPC). iii)As reported, at 12:43 hrs, 400 KV Uri_1(NH)-Amargarh (INDIGRID) (INDIGRID) Ckt-1 tripped on R-N phase to earth fault with fault distance of 12.5km and fault current of ~4.2kA from Amargarh end. iv)As per DR, fault current was ~4.55kA from Amargarh and ~1.42kA from Uri-I end. Fault was sensed in zone-1 from both the ends and fault cleared within ~50ms. v)Due to tripping of 400 KV Uri_1(NH)-Amargarh (INDIGRID) (INDIGRID) Ckt-1, 120 MW Uri-I HPS - UNIT 3 and 60 MW Uri-II HPS - UNIT 1 & 4 tripped due to loss of evacuation path and complete blackout occurred at 400kV Uri-I & II (NHPC). vi)As per PMU at Amargarh(PG), R-N phase to earth fault with successful A/R followed by another R-N phase to earth fault within reclaim time is observed with fault clearing time of 80ms. vii)As reported by NHPC, generation of approx 84 MW [9 MW at Uri-I(NH) and 75 MW at U | grid_india_gd/grid_events/2026-01-01
G00098 | 2026-01 | 21 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-01-24T15:22 | 2026-01-24T16:12 | 0.83 | 297 | 1180 | FALSE | FALSE | FALSE | FALSE | FALSE | 21 GD-1 Jammu and Kashmir 24-01-2026 15:22 24-01-2026 16:12 00:50 297 1180 0.55% 2.31% 54353 5105 9 i)During antecedent condition, Kashmir valley and Leh network (220kV Zainkote, Alusteng, Pampore, Delina, Kishenganga, Drass, Kargil, khalasti and 220kV Leh) were being fed from 400kV Uri-I HEP, 400kV | 21 GD-1 Jammu and Kashmir 24-01-2026 15:22 24-01-2026 16:12 00:50 297 1180 0.55% 2.31% 54353 5105 9 i)During antecedent condition, Kashmir valley and Leh network (220kV Zainkote, Alusteng, Pampore, Delina, Kishenganga, Drass, Kargil, khalasti and 220kV Leh) were being fed from 400kV Uri-I HEP, 400kV Uri-II HEP through 400kV Uri-I-Amargarh ckt-1 and 400kV Sambha-Amargarh D/C. 400 kV Uri-2 (NH) – Wagoora (PG) (PG) Ckt-1, 400kV Uri-I-Amargarh ckt-2, 400 kV Kishenpur – New Wanpoh (PG) Ckt-1, 3 & 4, 400 kV Baglihar (JK) – Kishenpur (PG) Ckt-3 and 400 kV New Wanpoh (PG) – Baglihar (JK) Ckt-1 were already under tripped condition. The aforementioned lines tripped on faults during heavy snowfall. ii)As reported, at 15:22 hrs, charging aƩempt of 400kV Uri-I-Amargarh ckt-2 was taken from Amargarh end. At the same time, B-N fault occurred on the line. During patrolling, it was found that OPGW fell on B-ph conductor. On this fault, SOTF protection at Amargarh end didn’t operate. iii)As fault didn’t clear from Amargarh end, 400kV Sambha-Amargarh D/C tripped from Sambha(PG) end. As per DR of Sambha(PG) en d, B-N fault in Z-2 with fault current of ~1.37kA is observed in each circuit. iv)As per PMU at Kishenpur(PG) and DR files of Sambha(PG), B-N fault with delayed clearance of ~560 msec is observed. v)As per SCADA, change in demand of ~1180 MW is observed in J&K control area out of which ~1135 MW change in load is observed in Kashmir Valley Region. vi)400 kV Samba–Amargarh D/C were restored | grid_india_gd/grid_events/2026-01-01
G00099 | 2026-01 | 35 | GD-1 | Maharashtra | MH | Western | 2026-01-24T18:29 | 2026-01-24T19:00 | 0.52 | 410 | 10 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GD-1 Maharashtra 24-01-2026 18:29 24-01-2026 19:00 00:31 410 10 0.53% 0.01% 77110 70275 Partial Outage of 220 kV Uran (MH) S/S:At 18:29 hrs/24-01-2026, 220 kV Main Bus -1 tripped due to Generation Unit AO (120 MW) LBB tripping command extended from generation end. Hence bus bar protection operate | 13 GD-1 Maharashtra 24-01-2026 18:29 24-01-2026 19:00 00:31 410 10 0.53% 0.01% 77110 70275 Partial Outage of 220 kV Uran (MH) S/S:At 18:29 hrs/24-01-2026, 220 kV Main Bus -1 tripped due to Generation Unit AO (120 MW) LBB tripping command extended from generation end. Hence bus bar protection operated at 220kV Uran Substation. 1. 220kV Uran Bus-1 2. 220 kV Uran–Apta 4 3. 220 kV Uran–Apta 2 4. 220 kV Uran–Ulwe 5. 220 kV Uran–ONGC Line 6. Uran Unit-5 7. Uran Unit-6 8. Uran Unit-7 9. Uran Unit-8 10. Uran Unit-A0 11. Uran Unit-B0 | grid_india_gd/grid_events/2026-01-01
G00100 | 2026-01 | 36 | GD-1 | Gujarat | GJ | Western | 2026-01-25T02:22 | 2026-01-25T05:23 | 3.02 | 270 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 270 MW occurred at Nakhatrana due to loss of evacuation path. | 14 GD-1 Gujarat 25-01-2026 02:22 25-01-2026 05:23 03:01 270 - 0.42% - 64679 52971 Complete Outage of 220 kV Nakhatrana(Adani) S/S: At 02:22 Hrs/ 25-01-2026, 220 KV Bhuj II-Nakhatrana & 220 KV Nakhatrana-Dedhiya tripped on Over Current Protection. 220 KV Bhuj II-Nakhatrana line did not trip from Bhuj II end. Generation loss of 270 MW occurred at Nakhatrana due to loss of evacuation path. 1. 220 KV Bhuj II-Nakhatrana2. 220 KV Nakhatrana-Dedhiya | grid_india_gd/grid_events/2026-01-01
G00101 | 2026-01 | 37 | GD-1 | Gujarat | GJ | Western | 2026-01-26T08:45 | 2026-01-26T12:07 | 3.37 | 302 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 302 MW occured at Khavda PSS-2 due to loss of evacualtion path. | 15 GD-1 Gujarat 26-01-2026 08:45 26-01-2026 12:07 03:22 302 - 0.39% - 76681 71000 Complete Outage of 400 kV NTPC Khavda PSS-2 S/S: At 08:45 hrs/ 26-01-2026, The 400kV KPSS-2–KPS1 line tripped due to bus bar protection operation on 400kV Khavda PSS-2 Bus-1 & Bus-II. Flashover on bus coupler isolator 89A has operated bus-bar protection. Generation loss of 302 MW occured at Khavda PSS-2 due to loss of evacualtion path. 1. 400kV Khavda PSS-2-KPS I 2. 400kV Khavda PSS-2 Bus 1 3. 400kV Khavda PSS-2 Bus 2 4. 400/33 kV Khavda PSS-2 ICT 1 5. 400/33 kV Khavda PSS-2 ICT 2 6. 400/33 kV Khavda PSS-2 ICT 3 7. 400/33 kV Khavda PSS-2 ICT 4 8. 400kV Bus-coupler at Khavda PSS-2 9. 765/400 kV Khavda PS-1 ICT-7 | grid_india_gd/grid_events/2026-01-01
G00102 | 2026-01 | 22 | GD-1 | Delhi | DL | Northern | 2026-01-27T10:13 | 2026-01-27T10:40 | 0.45 | 0 | 846 | FALSE | FALSE | FALSE | FALSE | FALSE | 1)220kV Bawana-Rohini-I line-I 2)220kV Bawana-Rohini-I line-II 3)400/220kV 315 MVA ICT-1 at Bawana(DTL) 4)400/220kV 315 MVA ICT-2 at Bawana(DTL) 5)400/220kV 315 MVA ICT-4 at Bawana(DTL) 6)400/220kV 315 MVA ICT-6 at Bawana(DTL) 7)220kV Bawana-Rohini-II line-II 8)220kV Bawana-Shalimarbagh line-I 9)220kV Bawana-Shalimarbagh line-II 10)220/33kV 100 MVA ICT-1 at Shalimarbagh(DTL) 11)220/66kV 160 MVA IC | 22 GD-1 Delhi 27-01-2026 10:13 27-01-2026 10:40 00:27 0 846 0.00% 1.33% 566 33 63510 i)400kV Bawana(DTL) S/s has one and half breaker bus scheme at 400kV level and double main & transfer bus scheme at 220kV level. ii)During antecedent condition, loading on 400/220kV 315 MVA ICT-1, 2, 3, 4, 5 & 6 at Bawana(DTL) were 154 MW, 155 MW, 147 MW, 150 MW, 130 MW & 130 MW respectively. iii)As reported, at 10:13 hrs, R-N fault occurred on 220kV Bawana-Rohini-I line-I & II due to snapping of OPGW . On this fault distance protection at both the ends operated and line tripped however R-ph pole at Bawana end of Ro hini-I line-I (connected at 220kV bus-1) got stuck. This further led to LBB operation however due to error in isolator status of Rohini-I line-I feeder, desired operation of LBB protection didn’t occur. iv)As the fault was persisting, oil leakage in R-ph CT of 220kV Bawana-Rohini-I line-I also started and created bus fault. This led to operation of 220kV bus bar protection resulted into tripping of 220kV Bawana-Shalimarbagh line-I & II and 220kV Bawana-Rohini-II line-II. v)At the same time, 400/220kV 315 MVA ICT-1, 2, 4 & 6 at Bawana(DTL) also tripped on overcurrent protection operation. 220/33kV 100 MVA ICT-1 at Shalimarbagh(DTL) and 220/66kV 160 MVA ICT-1 & 2 at Rohini-II(DTL) also tripped due to overcurrent earth fault protection. vi)As per PMU at Bawana(DTL), R-N phase to earth fault with delayed clearance of ~1480 msec is observed. vii)As per SCADA, change in demand of ~560MW | grid_india_gd/grid_events/2026-01-01
G00103 | 2026-01 | 44 | GI-1 | Andhra Pradesh | AP | Southern | 2026-01-29T10:48 | 2026-01-29T12:11 | 1.38 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | The triggering incident is the spurious LBB initiation in the lines during the checking of DC earth fault due to which LBB Re trip operated and tripped the lines. | 12 GI-1 ANDHRA PRADESH 29-01-2026 10:48 29-01-2026 12:11 01:23 0 0 0.00% 0.00% 57338.57 62415. 86 Tripping of 220kV Bus-1 of Lower Sileru of APGENCO 220kV LOWER_SILERU is under bus split condition where in 220kV Bus-1 at LOWER_SILERU is connected with 220KV-ASUPAKA-LOWER_SILERU-1 and 220KV- LOWER_SILERU-Chintur-1. The triggering incident is the spurious LBB initiation in the lines during the checking of DC earth fault due to which LBB Re trip operated and tripped the lines. Tripping of both 220KV-ASUPAKA-LOWER_SILERU-1 and 220KV-LOWER_SILERU-Chintur-1 led to the Tripping of 220kV Bus-1 of Lower Sileru of APGENCO 220KV-ASUPAKA-LOWER_SILERU-1, 220KV-LOWER_SILERU- Chintur-1 | grid_india_gd/grid_events/2026-01-01
G00104 | 2026-01 | 45 | GI-2 | Andhra Pradesh | AP | Southern | 2026-01-30T11:08 | 2026-01-30T11:29 | 0.35 | 287 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GI-2 ANDHRA PRADESH 30-01-2026 11:08 30-01-2026 11:29 00:21 287 0 0.00% 0.00% 59761.43 6233 2.93 Tripping of 400kV Bus-1 of Simhadri TPS of NTPC The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection ope | 13 GI-2 ANDHRA PRADESH 30-01-2026 11:08 30-01-2026 11:29 00:21 287 0 0.00% 0.00% 59761.43 6233 2.93 Tripping of 400kV Bus-1 of Simhadri TPS of NTPC The triggering incident is the Y-ph CT failure of 412Bay (Main Bay connected to 400kV Simhadri-Kalpakka-3) at Simhadri leading to Bus Bar protection operation and tripping of all the main breakers connected to 400kV Bus-1 of Simhadri TPS. During which due to the delay in tripping of TEED protection led to the delay in clearing of the fault and also Z2 was sensed in remote end. During the same time 400kV Khammam-Kalpakka tripped only at Khammam end on Z2 due to the delay in clearing of fault. Subsequently 400kV Simhadri-Kalpakka-3 line tripped on Z2 at Kalpakka end. After which due to OPGW cable cut 400kV Simhadri-Kalpakka-4 and 400kV Gazuwaka-Kalpakka tripped. During the event Hinduja unit 2 tripped due to flame failure. 400KV-SIMHADRI-KALPAKKA-3, 220KV-KALPAKKA-BRANDIX- 1, 400KV-KALPAKKA-KHAMMAM_PG-1, 400KV-GAZUWAKA- KALPAKKA-1 | grid_india_gd/grid_events/2026-01-01
G00105 | 2026-01 | 38 | GD-1 | Gujarat | GJ | Western | 2026-01-30T19:00 | 2026-01-30T20:10 | 1.17 |  | 190 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GD-1 Gujarat 30-01-2026 19:00 30-01-2026 20:10 01:10 - 190 - 0.35% 68806 53589 Complete Outage of 220 kV Versova (AEML) S/S: At 19:00 Hrs/30-01-2026, 220 kV Versova (AEML) Buses 1&2 tripped on Bus bar protection operation. As reported by AEML, tripping was due only main-2 relay to mal-operated of | 16 GD-1 Gujarat 30-01-2026 19:00 30-01-2026 20:10 01:10 - 190 - 0.35% 68806 53589 Complete Outage of 220 kV Versova (AEML) S/S: At 19:00 Hrs/30-01-2026, 220 kV Versova (AEML) Buses 1&2 tripped on Bus bar protection operation. As reported by AEML, tripping was due only main-2 relay to mal-operated of Bus bar protection. Due to tripping of both the 220 kV buses, 220 kV Versova (AEML) went dark and 190 MW load loss occurred due to the event. () 2. 220 kV Versova (AEML) Bus 2 3. 220 kV Versova (AEML)- Boisar(MH) 4. 220 kV Versova (AEML)- Dahanu 5. 220 kV Versova (AEML)- Gorai 6. 220 kV Versova (AEML)- Ghodbunder 7. 220 kV Versova (AEML)- Goregaon 1 8. 220 kV Versova (AEML)- Goregaon 2 9. 220 kV Versova (AEML)- Versova (TPC) 1 10. 220 kV Versova (AEML)- Versova (TPC) 2 11. 220 kV Versova (AEML) Bus coupler 12. 220/33 kV Versova (AEML) 100 MVA ICT 1 13. 220/33 kV Versova (AEML) 100 MVA ICT 2 14. 220/33 kV Versova (AEML) 100 MVA ICT 3 15. 220/33 kV Versova (AEML) 100 MVA ICT 4 16. 220/33 kV Versova (AEML) 125 MVA ICT 5 | grid_india_gd/grid_events/2026-01-01
G00106 | 2026-01 | 46 | GI-2 | Andhra Pradesh | AP | Southern | 2026-01-31T18:04 | 2026-01-31T21:20 | 3.27 | 450 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | During the same time due to outage of tie breaker led to the tripping of Unit-1 at Simhadri leading to a generation loss of 450MW SIMHADRI - 400KV - Bus 1, 420KV/21KV SIMHADRI-GT-1, 400KV-VEMAGIRI_PG-SIMHADRI-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 14 GI-2 ANDHRA PRADESH 31-01-2026 18:04 31-01-2026 21:20 03:16 450 0 0.01% 0.00% 49180.66 4900 4.59 Tripping of 400kV Bus-1 at Simhadri TPS of NTPC The triggering incident is the testing activity of CT after replacement of CT in 412 Bay at Simhadri TPS. Due to human error of testing activities, inadvertently current injection in the secondary side led to the operation BBP operation due to the imbalance and tripping of 400kV Bus-1 at Simhadri TPS. During the same time due to outage of tie breaker led to the tripping of Unit-1 at Simhadri leading to a generation loss of 450MW SIMHADRI - 400KV - Bus 1, 420KV/21KV SIMHADRI-GT-1, 400KV-VEMAGIRI_PG-SIMHADRI-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-01-01
G00107 | 2026-01 | 39 | GD-1 | Gujarat | GJ | Western | 2026-01-31T23:53 | 2026-02-01T02:08 | 2.25 | 1 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 1 MW reported due to loss of evacuation path. | 17 GD-1 Gujarat 31-01-2026 23:53 01-02-2026 02:08 02:15 1 - 0.00% - 66968 55542 Complete Outage of 220kV Manja Wind RE S/S :At 23:53 Hrs/31-01-2026, 220 Jamkhambaliya – Manja line tripped due to overvoltage protection operation. Generation loss of 1 MW reported due to loss of evacuation path. 1. 220 Jamkhambaliya – Manja line 2. 220/33 Manja KV ICT-1 3. 220/33 Manja KV ICT-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 KARNATAKA 05-01-2026 02:50 05-01-2026 03:35 00:45 129 53 0.00% 0 .00% 33775 39552 Complete outage of 220kV Chikkodi SS of KTPCL As per the reports submitted, the triggering incident is the failure of R-ph PT of 220kV Bus-1 at Chikkodi end, during which all the elements connected to Chikkodi tripped leading to complete outage of 220kV Chikkodi SS 220KV-CHIKKODI-KANAGALA-1, 220KV-CHIKKODI- KANAGALA-2, 220KV-CHIKKODI-KUDACHI-1, 220KV- CHIKKODI-KUDACHI-2, 220KV-CHIKKODI-MUGHALKHOD-1, 220KV-CHIKKODI-MUGHALKHOD-2 2 GD - 1 TAMILNADU 13-01-2026 06:17 13-01-2026 07:32 01:15 0 0 0.00% 0.00 % 42213 47477 Complete Outage of 230kV Sprng Pugalur Wind station The triggering incident was R-G fault in 230KV-PUGALUR-SPRING_PUGALUR-1 line due to suspected R-phase insulator flash over. At Pugalur end, the fault was sensed in zone-1, A/R operated and the line was holding. At Sprng_Pugalur end, the fault was sensed in carrier aided zone-2 and the | grid_india_gd/grid_events/2026-01-01
G00108 | 2026-02 | 15 | GD-1 | Gujarat | GJ | Western | 2026-02-01T05:44 | 2026-02-01T07:23 | 1.65 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | No generation loss occurred at Gandhar/Jhanor (NTPC) gas power plant during the event. | 1 GD-1 Gujarat 01-02-2026 05:44 01-02-2026 07:23 01:39 - - - - 70374 56554 Complete outage of 400/220 kV Gandhar/Jhanor (NTPC): At 05:44 hrs / 01-02-2026, 220 kV Gandhar-Bus-1&2 tripped on Busbar protection operation. The Busbar protection operated for a R-E fault in Zone-1 of 220 kV- Gandhar-Zagadiya-1 (19 km from Gandhar) which is undesirable. On inspection, it was found that CT cable between CT marshalling box to Busbar protection panel was faulty (armoured screen was damaged). The station has Double Main and Transfer bus scheme. No generation loss occurred at Gandhar/Jhanor (NTPC) gas power plant during the event. Busbar relays at 220 kV Jhanor end is of REB 670 make of year 2022 (same relay is used for busbar protection of both buses) and type low impedance. The fault resulted in differential current and activation of busbar protection. 1. 220 kV Gandhar-Jhagadiya-1 2. 220 kV Gandhar-Bus-1 3. 220 kV Gandhar-Bus-2 4. 400/220 kV Gandhar-ICT-1 5. 400/220 kV Gandhar-ICT-2 6. 220 kV Gandhar-Haldarwa-1 7. 220 kV Gandhar-Haldarwa-2 8. 220 kV Gandhar-Haldarwa-3 9. 220/33 kV Gandhar-ICT-1 | grid_india_gd/grid_events/2026-02-01
G00109 | 2026-02 | 16 | GD-1 | Gujarat | GJ | Western | 2026-02-01T15:13 | 2026-02-01T21:01 | 5.8 | 27 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, generation loss of 27 MW occurred at 220 kV Nanavalka (Alfnar) station. | 2 GD-1 Gujarat 01-02-2026 15:13 01-02-2026 21:01 05:48 27 - 0.04% - 72920 69764 Complete outage of 220 kV Nanavalka (alfanar): At 15:13 Hrs/01-02-2026, 220kV Bhuj- Nanavalka (Alfanar) line tripped on Bph-E fault. During inspection no abnormality found in line. Due to loss of evacuation path, generation loss of 27 MW occurred at 220 kV Nanavalka (Alfnar) station. 1. 220 kV Nanavalka(Alfanar) - Bhuj S/C 2. 220/33kV Alfanar ICT-1 3. 220/33kV Alfanar ICT-2 | grid_india_gd/grid_events/2026-02-01
G00110 | 2026-02 | 1 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-02-03T15:09 | 2026-02-03T15:49 | 0.67 | 0 | 267 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-1 Jammu and Kashmir 03-02-2026 15:09 03-02-2026 15:49 00:40 0 267 0.00% 0.50% 52157 53368 i)220/132kV Delina(JK) S/s has double main and transfer bus scheme at 220kV level and 220kV Kishenganga(NH) has double main bus scheme at 220kV level. ii)During antecedent condition, 220 KV Kishenganga(NH) | 1 GI-1 Jammu and Kashmir 03-02-2026 15:09 03-02-2026 15:49 00:40 0 267 0.00% 0.50% 52157 53368 i)220/132kV Delina(JK) S/s has double main and transfer bus scheme at 220kV level and 220kV Kishenganga(NH) has double main bus scheme at 220kV level. ii)During antecedent condition, 220 KV Kishenganga(NH)-Delina(PDD) (PG) Ckt-1 & were carrying ~62 MW each from Kishenganga(NH) to Delina(JK). Only 110MW Unit-2 at Kishenganga(NH) was in running condition and was generating approx 103 MW. iii)As reported, at 15:09 hrs, 220 KV Kishenganga(NH)-Delina(PDD) (PG) Ckt-1 & 2 tripped on DT received from Delina(JK) end (exact nature of protection operated at Delina end and reason of the same yet to be received). iv)As per PMU at Amargarh(INDIGRID), no fault was observed in the system. v)As per SCADA, change in demand of approx 267 MW was observed in J&K control area. 1) 220 KV Kishenganga(NH)-Delina(PDD) (PG) Ckt-1 2) 220 KV Kishenganga(NH)-Delina(PDD) (PG) Ckt-2 | grid_india_gd/grid_events/2026-02-01
G00111 | 2026-02 | 2 | GD-1 | Uttar Pradesh | UP | Northern | 2026-02-04T13:07 | 2026-02-04T13:47 | 0.67 | 0 | 180 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Uttar Pradesh 04-02-2026 13:07 04-02-2026 13:47 00:40 0 180 0.00% 0.32% 56430 55395 i)400/220kV Bareilly(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)During antecedent condition, 400/220KV 315 MVA ICT-1 at Bareilly(UP) was already under planned shutdown. | 2 GD-1 Uttar Pradesh 04-02-2026 13:07 04-02-2026 13:47 00:40 0 180 0.00% 0.32% 56430 55395 i)400/220kV Bareilly(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)During antecedent condition, 400/220KV 315 MVA ICT-1 at Bareilly(UP) was already under planned shutdown. iii)As reported, at 13:07 hrs, fault occurred on 400kV Y-ph of Bus-2 at Bareilly(UP) due to a metallic kite thread. On this fault, 400kV static bus bar protection at Bareilly(UP) did not operate. iv)This led to tripping of all 400kV lines connected to both the buses on zone-2 protection operation from remote end (as confirmed from DR). v)On this fault, 400/220kV 315 MVA ICT-3 at Bareilly(UP) tripped on LV side backup directional earth fault relay operation. However, 400/220kV 315 MVA ICT-2 at Bareilly(UP) didn’t trip as backup relay did not operate. vi)Due to this, all 220kV lines connected to Bareilly(UP) tripped on zone-3 or directional E/F protection operation from remote end except 220kV Bareilly(UP) -CB Ganj Ckt-2 and 220kV Bareilly(UP)-Pilbhit Ckt-2 and complete blackout occurred at 400/220kV Bareilly(UP). vii)As per SCADA SOE, 220/132kV 160 MVA ICT-1 & 2 at Dohna also tripped during the same time. As confirmed by SLDC UP , 220/132kV 160 MVA ICT-1 & 2 at Dohna tripped due to directional E/F protection operation. viii)As per DR and PMU at Bareilly(PG), Y-N phase to earth fault was observed with delayed fault clearing time of 400 ms. ix)As per SCADA, no change in demand is obs | grid_india_gd/grid_events/2026-02-01
G00112 | 2026-02 | 17 | GD-1 | Gujarat | GJ | Western | 2026-02-05T16:39 | 2026-02-05T21:24 | 4.75 | 55 |  | FALSE | FALSE | FALSE | FALSE | FALSE | As a result of loss of evacuation path, there was a generation loss of 55 MW at the 220/33 kV Alfanar Valka nana station. | 3 GD-1 Gujarat 05-02-2026 16:39 05-02-2026 21:24 04:45 55 - 0.07% - 81165 73131 Complete outage of 220 kV Nanavalka (alfanar): At 16:39 hrs/05.02.2026, the 220 kV Alfanar–Valka nana Bhuj line tripped due to a B–E fault due to manually tripping of line by miscreant at tower no. 16/1 by throwing conducting object on line. The issue was resolved with the help of local police authorities, and the line was restored. Thereafter, the 220 kV Bhuj–Alfanar breaker and the Alfanar–Valkanana PSS breaker were charged. As a result of loss of evacuation path, there was a generation loss of 55 MW at the 220/33 kV Alfanar Valka nana station. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C 2. 220/33kV Alfanar ICT-1 3. 220/33kV Alfanar ICT-2 | grid_india_gd/grid_events/2026-02-01
G00113 | 2026-02 | 29 | GD-1 | BSPTCL |  |  | 2026-02-06T09:35 | 2026-02-06T09:56 | 0.35 | 0 | 390 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 BSPTCL 06-02-2026 09:35 06-02-2026 09:56 00:21 0 390 0.00% 1.62% 32955 24070 At 09:35 Hrs, bus fault was occurred at 220kV Begusarai S/s due to snapping of Y-phase jumper between the CB and CT of 220 kV BTPS line-2 which led to tripping of all emanating line from 220kV Begusarai S/s in Z-4 pr | 1 GD-1 BSPTCL 06-02-2026 09:35 06-02-2026 09:56 00:21 0 390 0.00% 1.62% 32955 24070 At 09:35 Hrs, bus fault was occurred at 220kV Begusarai S/s due to snapping of Y-phase jumper between the CB and CT of 220 kV BTPS line-2 which led to tripping of all emanating line from 220kV Begusarai S/s in Z-4 protection (Bus bar protection was not in service). 220kV Begusarai S/s became dead. Total load loss of 390 MW reported at 220kV Begusarai S/s. 220KV BTPS Begusarai- 1 220KV BTPS Begusarai- 2 220KV Saharsa Begusarai- 1 220KV Saharsa Begusarai- 2 220KV Khagaria Begusarai- 1 220KV Khagaria Begusarai- 2 220KV Samastipur Begusarai- 1 220KV Samastipur Begusarai- 2 220KV IOCL Begusarai- 1 220KV IOCL Begusarai- 2 | grid_india_gd/grid_events/2026-02-01
G00114 | 2026-02 | 24 | GI-2 | Karnataka | KA | Southern | 2026-02-07T06:28 | 2026-02-07T07:31 | 1.05 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-2 KARNATAKA 07-02-2026 06:28 07-02-2026 07:31 01:03 0 0 0.0 % 0.0 % 45270.4 54013.64 Tripping of 400kV Bus-2 of 400kV Talaguppa SS of KPTCL As per the reports submitted, while hand-tripping the 125 MVAR Bus Reactor-2, the Bus Reactor-2 circuit breaker (CB-410R.52) experienced a flashover on the | 9 GI-2 KARNATAKA 07-02-2026 06:28 07-02-2026 07:31 01:03 0 0 0.0 % 0.0 % 45270.4 54013.64 Tripping of 400kV Bus-2 of 400kV Talaguppa SS of KPTCL As per the reports submitted, while hand-tripping the 125 MVAR Bus Reactor-2, the Bus Reactor-2 circuit breaker (CB-410R.52) experienced a flashover on the R-phase limb, and the R-phase lightning arrester also flashed over. Immediately, it was suspected that the LBB protection of the bus reactor operated, resulting in the tripping of all main breakers connected to the 400 kV Talaguppa Bus-2. However, a DT was sent to the remote ends of the 400 kV Talaguppa Hassan line and 400 kV Talaguppa Nelamangala lines. At the remote ends, the lines tripped, and due to a rise in voltage, the overvoltage protection operated after 8 seconds. Subsequently, a DT was sent to the Talaguppa end, causing the tripping of the tie breakers of these lines, and the lines tripped. 400KV-TALGUPPA-HASSAN-1, 400KV-NELAMANGALA- TALGUPPA-1, TALGUPPA - 400KV - Bus 2 | grid_india_gd/grid_events/2026-02-01
G00115 | 2026-02 | 3 | GD-1 | Rajasthan | RJ | Northern | 2026-02-10T15:55 | 2026-02-10T23:32 | 7.62 | 165 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per PMU and SCADA, solar generation loss of approx 165 MW was observed at XL XERGI(IP). | 3 GD-1 Rajasthan 10-02-2026 15:55 10-02-2026 23:32 07:37 165 0 0.30% 0.00% 54610 54195 i)Generation of 220kV XL XERGI(IP) station evacuates through 220 KV Fatehgarh_III(PG)-XL_XPPL_SL_Ftg3(PG) (XL_XPPL) Ckt which is further connected to 220/33 kV 213 MVA ICT 1 & 2 at XL_XPPL_SL_Ftg3(PG). ii)During antecedent condition, 220kV XL XERGI(IP) station was generating approx 165 MW (as per PMU and SCADA). iii)As reported, at 15:55 hrs, 220 KV Fatehgarh_III(PG)-XL_XPPL_SL_Ftg3(PG) (XL_XPPL) Ckt auto-reclosed from Fatehgarh_III(PG) end on R-N phase to earth fault (exact reason, nature and location of fault yet to be shared). iv)During auto-recloser operation, unbalanced current flow through neutral led to tripping of both 220/33 kV 213 MVA ICT 1 & 2 at XL_XPPL_SL_Ftg3(PG) on O/C E/F protection operation. This resulted into complete blackout of 220kV XL XERGI(IP). v)As per PMU at Fatehgarh3(PG), R-N phase to earth fault was observed with fault clearing time of 80ms. Voltage dipped upto 0.57 pu during fault. vi)As per PMU and SCADA, solar generation loss of approx 165 MW was observed at XL XERGI(IP). As per SCADA, change in NR total generation of approx 186 MW was observed. 1) 220/33 kV 213 MVA ICT 1 at XL_XPPL_SL_Ftg3(PG) 2) 220/33 kV 213 MVA ICT 2 at XL_XPPL_SL_Ftg3(PG) | grid_india_gd/grid_events/2026-02-01
G00116 | 2026-02 | 25 | GI-2 | Karnataka | KA | Southern | 2026-02-12T07:26 | 2026-02-12T14:58 | 7.53 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-2 KARNATAKA 12-02-2026 07:26 12-02-2026 14:58 07:32 0 0 0.0 % 0.0 % 54560.05 63294.98 Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operate | 10 GI-2 KARNATAKA 12-02-2026 07:26 12-02-2026 14:58 07:32 0 0 0.0 % 0.0 % 54560.05 63294.98 Tripping of 400kV Bus-2 of 400kV Yelahanka_PG SS of PGCIL SR-2 As per the reports submitted, the triggering incident was Y-G fault in 400kV Bus-2 of 400kV Yelahanka_PG SS. Immediately, 400kV Bus-2 BBP operated and all the elements connected to the bus tripped. 400KV/220KV YELHANKA-ICT-2, 400KV-YELHANKA- NELAMANGALA-1, YELHANKA - 400KV - Bus 2, 400KV- TUMKUR-YELHANKA-2 | grid_india_gd/grid_events/2026-02-01
G00117 | 2026-02 | 18 | GI-1 | Gujarat | GJ | Western | 2026-02-12T08:42 | 2026-02-12T09:00 | 0.3 |  | 72 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-1 Gujarat 12-02-2026 08:42 12-02-2026 09:00 00:18 - 72 - 0.09% 84876 78405 Partial outage of 220kV Vapi (GJ): At 08:42 Hrs/12-2-2026, 220kV Vapi(GJ) Bus 2 and all the connected elements tripped on LBB operation of 220/33 kV Vapi(GJ) ICT 3. As reported by SLDC Gujarat, HV side Y phase CT of 220/ | 4 GI-1 Gujarat 12-02-2026 08:42 12-02-2026 09:00 00:18 - 72 - 0.09% 84876 78405 Partial outage of 220kV Vapi (GJ): At 08:42 Hrs/12-2-2026, 220kV Vapi(GJ) Bus 2 and all the connected elements tripped on LBB operation of 220/33 kV Vapi(GJ) ICT 3. As reported by SLDC Gujarat, HV side Y phase CT of 220/33 kV Vapi(GJ) ICT 3 failed & Differential protection operated. Due to the non-tripping of main bay on differential protection operation, LBB protection operated and resulted in tripping of 220 kV Vapi(GJ) Bus 2. 220 kV Vapi(GJ)- Vapi II (Sterlite) 1 (tripped only at Vapi (GJ) end), 220 kV Vapi(GJ)- Chikli, 220/66 kV Vapi(GJ) ICT 3 & 220 kV Vapi(GJ) Bus coupler tripped during the event. Due to the tripping of 220/66 kV Vapi(GJ) ICT 3 (220/66 kV Vapi(GJ) ICT 1 already under planned shutdown), loading on 220/66 kV Vapi(GJ) ICTs 2&4 exceeded and resulted in LTS operation at 08:58 Hrs. As reported by GETCO, load relief of 72 MW occurred due to LTS operation. 1. 220 kV Vapi(GJ) Bus 2 2. 220 kV Vapi(GJ)- Vapi II (Sterlite) 1 3. 220 kV Vapi(GJ)- Chikli 4. 220/66 kV Vapi(GJ) ICT 3 | grid_india_gd/grid_events/2026-02-01
G00118 | 2026-02 | 19 | GI-1 | Gujarat | GJ | Western | 2026-02-12T11:06 | 2026-02-12T12:45 | 1.65 | 20 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 20 MW occurred at 220 kV Dayapar (Inox) WPP. | 5 GI-1 Gujarat 12-02-2026 11:06 12-02-2026 12:45 01:39 20 - 0.02% - 87854 81058 Partial outage of 220kV Dayapar(INOX): At 11:06 Hrs/12-02-2026, 220 kV Dayapar Bus 1 and all the connected elements tripped on Bus bar protection operation due to B phase Bus insulator flashover. 220 kV Bhuj- Dayapar 1, 220/33kV Dayapar ICTs 1, 2&3 and 220 kV Dayapar Bus coupler tripped during the event. Generation loss of 20 MW occurred at 220 kV Dayapar (Inox) WPP. 1. 220 kV Bhuj Dayapar 1 2. 220/33kV Dayapar ICT-1 3. 220/33kV Dayapar ICT-2 4. 220/33kV Dayapar ICT-3 | grid_india_gd/grid_events/2026-02-01
G00119 | 2026-02 | 4 | GD-1 | Uttar Pradesh | UP | Northern | 2026-02-13T10:37 | 2026-02-13T16:05 | 5.47 | 0 | 55 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GD-1 Uttar Pradesh 13-02-2026 10:37 13-02-2026 16:05 05:28 0 55 0.00% 0.08% 65720 68313 i)220/132/33kV Tundla(UP) has double main and transfer bus scheme at both 220kV level and 132kV level. There are two 220kV ckts connected to Tundla(UP), i.e., 220 kV Tundla(UP)-Firozabad(PJFTL) (UP) Ckt and 220 | 4 GD-1 Uttar Pradesh 13-02-2026 10:37 13-02-2026 16:05 05:28 0 55 0.00% 0.08% 65720 68313 i)220/132/33kV Tundla(UP) has double main and transfer bus scheme at both 220kV level and 132kV level. There are two 220kV ckts connected to Tundla(UP), i.e., 220 kV Tundla(UP)-Firozabad(PJFTL) (UP) Ckt and 220 kV Agra(PG)-Tundla(UP) (UP) Ckt. ii)As reported, at 10:37 hrs, while taking the approved shutdown of 220 kV Tundla(UP)-Firozabad(PJFTL) (UP) Ckt, 220 kV Agra(PG)-Tundla(UP) (UP) Ckt tripped from Agra(PG) on DT received. This led to complete blackout of 220/132/33kV Tundla(UP). iii)As per PMU at Agra(PG), no fault was observed in the system. iv)As per SCADA, change in demand of approx 108 MW was observed in UP control area. However, as reported by SLDC UP , load loss of approx 55 MW occurred in UP control area v)Charging aƩempt of 220 kV Agra(PG)-Tundla(UP) (UP) Ckt was made at 11:24 hrs, but line did not hold and tripped again on DT received. vi)Load was restored after charging of 220 kV Tundla(UP)-Firozabad(PJFTL) (UP) Ckt at 11:58 hrs. 1) 220 kV Agra(PG)-Tundla(UP) (UP) Ckt | grid_india_gd/grid_events/2026-02-01
G00120 | 2026-02 | 20 | GD-1 | Gujarat | GJ | Western | 2026-02-16T11:27 | 2026-02-16T12:09 | 0.7 | 40 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Solar RE generation loss of around 40 MW in the first disturbance and 114 MW in the second disturbance reported due to loss of evacuation path. | 6 GD-1 Gujarat 16-02-2026 11:27 16-02-2026 12:09 00:42 40 - 0.05% - 88407 79023 Complete outage of 220kV Shajapur Unit 6 & 7: At 11:27 hrs/ 16-02-2026, 220 kV Shajapur-U6-ShajapurU7 line tripped on 3 phase differential protection operation which was restored at 12:09 Hrs and again tripped at 12:35 Hrs on 3 phase differential protection operation. Solar RE generation loss of around 40 MW in the first disturbance and 114 MW in the second disturbance reported due to loss of evacuation path. 1. 220kV Shajapur U6-Shajapur U7 | grid_india_gd/grid_events/2026-02-01
G00121 | 2026-02 | 5 | GI-2 | Rajasthan | RJ | Northern | 2026-02-16T11:33 | 2026-02-16T11:57 | 0.4 | 2491 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | viii)As per SCADA, generation loss of approx 650 MW at RAPP-D and pumping loss of approx 221 MW at Tehri PSP was observed. | 5 GI-2 Rajasthan 16-02-2026 11:33 16-02-2026 11:57 00:24 2491 0 4.23% 0.00% 58824 63345 i)During antecedent condition, 700MW RAPS-D - UNIT 1 was generating approx 650 MW and 250 MW (PSP) TEHRI HPS - UNIT 5 & 7 were pumping approx 265 MW each. 250 MW (PSP) TEHRI HPS - UNIT 6 started pumping at around 11:30 hours and was gradually increasing pumping. Just before tripping, it was pumping approx 221 MW. NR total solar generation was approx 28642 MW among which Rajasthan solar generation was approx 6544 MW. ii)As reported, at 11:33 hrs, 250 MW (PSP) TEHRI HPS - UNIT 6 tripped on QSD (Quick Shut down) due to deadband timeout (exact reason yet to be shared). iii)During the same time, 700MW RAPS-D - UNIT 1 also tripped due to Turbine-Generator (TG) trip on reverse power during MW hunting (exact reason yet to be shared). iv)As per SCADA, Line CB at A43RS(IP) end of 400 KV AzurePSS43 SL_BKN_PG-AzureRS43 SL_BKN_PG (Azure) Ckt opened at 11:34:11.929 hrs and again closed at 11:34:50.173 hrs. However, Azure43 verbally reported that there was data issue at A43RS(IP) during that time, no tripping or auto-reclosing occurred during that time (written confirmation yet to be received from Azure43). v)As per SCADA SOE, 33kV Feeder and Block tripping was detected at A43RS_IP , ASPS2_IP and AVDAS_IP . vi)As per PMU at RAPP-C(NP), consecutive three 3-phase voltage dips were observed with voltage recovery time of 80 ms, 4360 ms and 80 ms. vii)As per SCADA, dip of approx 2062 MW occurred in NR total s | grid_india_gd/grid_events/2026-02-01
G00122 | 2026-02 | 6 | GD-1 | Punjab | PB | Northern | 2026-02-20T14:42 | 2026-02-20T14:55 | 0.22 | 286 | 176 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 286 MW occured at GGSTP Ropar(PS). | 6 GD-1 Punjab 20-02-2026 14:42 20-02-2026 14:55 00:13 286 176 0.50% 0.31% 57594 56386 i)220kV GGSTP Ropar(PS) has double main bus scheme at 220kV level. ii)During antecedent condition, 210 MW Guru Gobind Singh TPS (Ropar) - UNIT 4 & 5 were only in running condi tion and generating approx 143 MW each. iii)As reported, at 14:42 hrs, during the changing of tripology and testing of bus bar differential relay, LBB of Bus Coupler operated. iv)Due to this, both the 220kV buses at GGSTP Ropar(PS) tripped and all the elements connected at 220kV GGSTP Ropar(PS) tripped. This led to complete blackout of 220/132kV GGSTP Ropar(PS) S/s. v)As per PMU at Jalandhar(PG), no fault was observed in the system; however voltage dip observed in all three phases. vi)As per SCADA, change in demand of approx 176 MW in Punjab control area was observed. Generation loss of approx 286 MW occured at GGSTP Ropar(PS). 1) 220kV GGSTP Ropar(PS)-Ropar Ckt-1 2) 220kV GGSTP Ropar(PS)-Ropar Ckt-2 3) 220kV GGSTP Ropar(PS)-Gobingarh Ckt-1 4) 220kV GGSTP Ropar(PS)-Gobingarh Ckt-2 5) 220kV GGSTP Ropar(PS)-Jadla Ckt-1 6) 220kV GGSTP Ropar(PS)-Jadla Ckt-2 7) 220kV GGSTP Ropar(PS)-Kharar Ckt 8) 220kV GGSTP Ropar(PS)-Mohali Ckt 9) 220kV GGSTP Ropar(PS)-Bassi Pathana Ckt 10) 220kV GGSTP Ropar(PS)-Wazirabad Ckt 11) 220/132kV 100 MVA ICT-1 at GGSTP Ropar(PS) 12) 220/132kV 100 MVA ICT-2 at GGSTP Ropar(PS) 13) 220/33kV ST-4 at GGSTP Ropar(PS) 14) 210 MW Guru Gobind Singh TPS (Ropar) - UNIT 4 15) 210 MW Guru Gobind Singh TPS (Ro | grid_india_gd/grid_events/2026-02-01
G00123 | 2026-02 | 21 | GD-1 | Gujarat | GJ | Western | 2026-02-20T17:28 | 2026-02-21T14:43 | 21.25 | 10 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 10 MW occurred at 220kV Roha-Naranpar S/S due to loss of evacuation path. | 7 GD-1 Gujarat 20-02-2026 17:28 21-02-2026 14:43 21:15 10 - 0.01% - 80254 71969 Complete outage of 220kV Roha Naranpar (GIWEL-III): At 17:28hrs /20-02-2026, 220 kV Bhuj- Roha-Naranpar GIWEL(Wind RE) single circuit tripped due to B-phase-E fault. Generation loss of 10 MW occurred at 220kV Roha-Naranpar S/S due to loss of evacuation path. 1. 220 kV Bhuj-Roha-Naranpar 2. 220 kV Roha-Naranpar ICT-1 3. 220 kV Roha-Naranpar ICT-2 | grid_india_gd/grid_events/2026-02-01
G00124 | 2026-02 | 22 | GD-1 | Madhya Pradesh | MP | Western | 2026-02-21T09:16 | 2026-02-21T10:15 | 0.98 | 53 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Solar RE generation loss of around 53 MW reported due to loss of evacuation path. | 8 GD-1 Madhya pradesh 21-02-2026 09:16 21-02-2026 10:15 00:59 53 - 0.06% - 88388 76653 Complete outage of 220kV Shajapur Unit 6 & 7: At 09:16 Hrs/21-02-2026, 220kV Shajapur Unit 7 (Dehripal) - Shajapur Unit 6 (Burley) line tripped during R-Y-B phase fault in 33kV feeder at Shajapur Unit 6. Due to tripping of this line, 220 kV Shajapur U6 (Burley) radially connected with 220 kV Shajapur Unit 7 went dark. Solar RE generation loss of around 53 MW reported due to loss of evacuation path. 1. 220kV Shajapur Unit 7 (Dehripal) - Shajapur Unit 6 (Burley) 2. 220KV/33 kV Shajapur Unit-6 (Burley) ICT-1 | grid_india_gd/grid_events/2026-02-01
G00125 | 2026-02 | 7 | GD-1 | Rajasthan | RJ | Northern | 2026-02-21T13:36 | 2026-02-21T15:05 | 1.48 | 1752 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per PMU, generation loss of approx 303 MW and 207 MW occurred at 220kV ABCRL(IP) and 220kV RSDCL PSS1 (NT) respectively. | 7 GD-1 Rajasthan 21-02-2026 13:36 21-02-2026 15:05 01:29 1752 0 3.19% 0.00% 54986 55351 i)Generation of 220kV ABCRL(IP) and 220kV RSDCL PSS1 (NT) station evacuate through 220 KV ABCRenew_RJ01_SL _BHD2_PG-Bhadla_2 (PG) (ABC RJ01) Ckt and 220 KV RSDCL(PSS1)_SL_BHD2 _PG-Bhadla_2 (PG) (RSDCL) Ckt. ii)During antecedent condition, 220kV ABCRL(IP) and 220kV RSDCL PSS1 (NT) station were generating approx 303 MW and 207 MW respectively (as per PMU). iii)As reported, at 13:36 hrs, 220 KV RSDCL(PSS1)_SL_BHD2 _PG-Bhadla_2 (PG) (RSDCL) Ckt tripped due to snapping of the Y-phase jumper at the Tower Loc. No. 25 (exact nature of protection operation yet to be shared). iv)During the same time, 220 KV ABCRenew_RJ01_SL _BHD2_PG-Bhadla_2 (PG) (ABC RJ01) Ckt also tripped on Y-B phase to phase fault (exact reason & location of fault and nature of protection operation yet to be shared). v)Due to tripping of 220 KV ABCRenew_RJ01_SL _BHD2_PG-Bhadla_2 (PG) (ABC RJ01) Ckt and 220 KV RSDCL(PSS1)_SL_BHD2 _PG-Bhadla_2 (PG) (RSDCL) Ckt, complete blackout occurred at 220kV ABCRL(IP) and 220kV RSDCL PSS1 (NT) due to loss of evacuation path. vi)As per PMU, generation loss of approx 303 MW and 207 MW occurred at 220kV ABCRL(IP) and 220kV RSDCL PSS1 (NT) respectively. vii)As per SCADA, at the same time, dip in NR total Solar Generation of approx 1752 MW among which dip in Rajasthan Solar Generation of approx 456 MW was observed. viii)Due to drop in solar generation, over-voltage situation occurred due to unload | grid_india_gd/grid_events/2026-02-01
G00126 | 2026-02 | 23 | GD-1 | Gujarat | GJ | Western | 2026-02-22T00:59 | 2026-02-25T21:31 | 92.53 | 35 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 35 MW occurred at Gadhisa Wind Power Plant (Renew Power) due to loss of evacuation path. | 9 GD-1 Gujarat 22-02-2026 00:59 25-02-2026 21:31 92:32 35 - 0.05% - 70283 60242 Complete outage of 220 kV Gadhsisa (Renew Power): At 00:59 hrs / 22-02-2026, 220 kV Bhuj-Gadhsisa-1 S/C tripped on B-E fault. Generation loss of 35 MW occurred at Gadhisa Wind Power Plant (Renew Power) due to loss of evacuation path. 1. 220kV Bhuj-Gadhsisa S/C 2. 220kV Gadhsisa Bus-1 3. 220kV Gadhsisa Bus-2 4. 220/33 kV 160MVA Gadhsisa ICT-1 Elements Tripped Details of Grid Events during the Month of February 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 KARNATAKA 02-02-2026 01:31 02-02-2026 01:52 00:21 75 39 0.0 % 0.0 % 36691.28 41498.83 Complete outage of 220kV Guttur SAS, Neelagunda and Tripping of 220kV Bus-1 of Guttur SS of KPTCL In the antecedent conditions, 220kV Neelagunda-Ittagi was under idle charged condition from Neelagunda end and hence 220kV Neelagunda is radially connected to 220kV Guttur SS. 220kV Guttur SAS is connected to Bus-1 at | grid_india_gd/grid_events/2026-02-01
G00127 | 2026-02 | 26 | GI-1 | TAMILNADU |  |  | 2026-02-22T12:48 | 2026-02-22T13:35 | 0.78 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-1 TAMILNADU 22-02-2026 12:48 22-02-2026 13:35 00:47 0 0 0.0 % 0.0 % 54626.83 61399.62 Tripping of 230kV Bus-2 of 230kV Kayathar SS of TANTRANSCO 230kV Kayathar SS is operating with double bus with bus coupler at 230kV level but all elements were connected to 230kV Bus-2. As per the reports sub | 11 GI-1 TAMILNADU 22-02-2026 12:48 22-02-2026 13:35 00:47 0 0 0.0 % 0.0 % 54626.83 61399.62 Tripping of 230kV Bus-2 of 230kV Kayathar SS of TANTRANSCO 230kV Kayathar SS is operating with double bus with bus coupler at 230kV level but all elements were connected to 230kV Bus-2. As per the reports submitted, the triggering incident was 230kV YB fault in 230kV Bus-2. Hence 230kV BBP operated and all elements connected in Bus-2 got tripped. 110kV side was in service during the event. 230KV-Chekkanurani-KAYATHAR(TN)-1, 230KV- KAYATHAR(TN)-KAYATHAR-1, 230KV-KAYATHAR(TN)- KAYATHAR-2, 230KV-KAYATHAR(TN)-KINNIMANGLAM-2, 230KV-KAYATHAR(TN)-SANGANERI-1, 230KV-KAYATHAR(TN)- TIRUNELVELI-1, 230KV-KAYATHAR(TN)-TTPS-2, 230KV- KAYATHAR(TN)-TTPS-AUTO-1, 230KV-KAYATHAR(TN)- UDAYATHOOR-1, 230KV-KAYATHAR(TN)-VEERANAM-1 | grid_india_gd/grid_events/2026-02-01
G00128 | 2026-02 | 9 | GD-1 | Rajasthan | RJ | Northern | 2026-02-22T16:24 | 2026-02-22T20:48 | 4.4 | 80 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per PMU and SCADA, solar generation loss of approx 80 MW was observed at 220kV Juniper Green(JGCPL)(IP). | 9 GD-1 Rajasthan 22-02-2026 16:24 22-02-2026 20:48 04:24 80 0 0.16% 0.00% 48966 46897 i)Generation of 220kV Juniper Green(JGCPL)(IP) station evacuates through 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt. ii)During antecedent condition, 220kV Juniper Green(JGCPL)(IP) station was generating approx 80 MW (as per PMU and SCADA). iii)As reported, at 16:24 hrs, 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt tripped from Bikaner_2(PG) end only, no CB tripping occurred at JGCPL(IP) end (exact reason of tripping yet to be shared by PG). iv)Due to tripping of 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt, complete blackout occurred at 220kV Juniper Green(JGCPL)(IP) due to loss of evacuation path. v)As per PMU at Bikaner2(PG), no fault was observed in the system. vi)As per PMU and SCADA, solar generation loss of approx 80 MW was observed at 220kV Juniper Green(JGCPL)(IP). 1) 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt | grid_india_gd/grid_events/2026-02-01
G00129 | 2026-02 | 8 | GD-1 | Rajasthan | RJ | Northern | 2026-02-22T17:08 | 2026-02-22T19:07 | 1.98 | 525 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | ISTS solar generation at that time was ~11,600 MW and Bikaner 2 generation at that time was ~1800 MW. | 8 GD-1 Rajasthan 22-02-2026 17:08 22-02-2026 19:07 01:59 525 0 1.19% 0.00% 44130 46136 i)Generation of 400kV SGEL(SJVN) and 220kV JGCPL(IP), KSP(NHPC), ASSPL(IP), RDUPL(IP), SRI4PL(IP), KREPL(IP), GEPL(IP), JREPL(IP), BTPSL(IP) & PGPL(IP) stations evacuate through individual single circuit lines from plants to Bikaner2(PG). ii)400 kV Bikaner_2 (PBTSL) – Bikaner (PG) Ckt-1 & 2 were taken under planned outage from 16:00 hrs on 22.02.2026 to 05.03.2026 for LILO of the 400 kV Bikaner_2 (PBTSL) – Bikaner (PG) D/C lines at 400 kV Bikaner-III substation. The outage code was issued by NRLDC at 16:21 hrs. Subsequently, the lines were opened at 16:40 hrs. ISTS solar generation at that time was ~11,600 MW and Bikaner 2 generation at that time was ~1800 MW. After opening of these lines, oscillations observed in the System Frequency from 16:44 hrs onward as per PMU frequency plots. However, no corresponding fluctuation was observed in the PMU voltage plots. Immediately after opening of 400 kV Bikaner_2 (PBTSL) – Bikaner (PG) D/C lines at 16:41 hrs, huge fluctuation in active power started in 300MW Karnisar NHPC and 200MW Renew Dinkar at 16:44 hrs. iii)With triggering of active power fluctuation in 300MW Karinsar NHPC and 200MW Renew Dinkar at 16:44 hrs, other RE plants also exhibited the continuous active power fluctuation but magnitude in other plants were comparatively lesser. iv)As reported, at 16:24 hrs, 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt tripped from Bikaner | grid_india_gd/grid_events/2026-02-01
G00130 | 2026-02 | 10 | GD-1 | Uttar Pradesh | UP | Northern | 2026-02-23T12:51 | 2026-02-23T13:13 | 0.37 | 0 | 295 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Uttar Pradesh 23-02-2026 12:51 23-02-2026 13:13 00:22 0 295 0.00% 0.50% 59263 58765 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)As reported, at 12:51 hrs, R-ph disc insulator of 400kV Bus-2 at Gorakhpur(UP) got damaged. iii)As per | 10 GD-1 Uttar Pradesh 23-02-2026 12:51 23-02-2026 13:13 00:22 0 295 0.00% 0.50% 59263 58765 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)As reported, at 12:51 hrs, R-ph disc insulator of 400kV Bus-2 at Gorakhpur(UP) got damaged. iii)As per DR, on this fault, bus bar protection operated (both zone-1 and zone-2) in both the buses of 400kV Gorakhpur(UP). iv)All the elements connected to both 400kV buses tripped and complete blackout occurred at 400/220kV Gorakhpur(UP). v)As per at Lucknow(PG), R-N phase to earth fault was observed with fault clearing time of 80 ms. vi)As per SCADA, change in demand of approx 270 MW was observed in UP control area. However, as reported by SLDC UP , load loss of approx 295 MW occurred in UP control area. 1) 400 KV Azamgarh-Gorakhpur (UP) Ckt 2) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-1 3) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-2 4) 400/220 kV 500 MVA ICT 1 at Gorakhpur(UP) 5) 400/220 kV 500 MVA ICT 2 at Gorakhpur(UP) 6) 400/220 kV 315 MVA ICT 3 at Gorakhpur(UP) 7) 400kV Bus-1 at Gorakhpur(UP) 8) 400kV Bus-2 at Gorakhpur(UP) | grid_india_gd/grid_events/2026-02-01
G00131 | 2026-02 | 27 | GI-2 | Karnataka | KA | Southern | 2026-02-24T04:27 | 2026-02-24T17:52 | 13.42 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-2 KARNATAKA 24-02-2026 04:27 24-02-2026 17:52 13:25 0 0 0.0 % 0.0 % 41779.77 50398.48 Tripping of 400kV Bus-2 at RTPS of KPCL The triggering incident is the B-G bus fault in 400kV Bus-2 at RTPS. All the main breakers connected to Bus-2 got tripped and led to the tripping of 400kV Bus-2 at RTPS | 12 GI-2 KARNATAKA 24-02-2026 04:27 24-02-2026 17:52 13:25 0 0 0.0 % 0.0 % 41779.77 50398.48 Tripping of 400kV Bus-2 at RTPS of KPCL The triggering incident is the B-G bus fault in 400kV Bus-2 at RTPS. All the main breakers connected to Bus-2 got tripped and led to the tripping of 400kV Bus-2 at RTPS. 400kV RTPS-Munirabad was only in service with the main breaker connected to Bus-2 and due to the tripping of the Bus-2 led to the tripping of 400kV RTPS-Munirabad line. All other elements were in service through 400kV Bus-1. 400KV-MUNIRABAD-RTPS-1, RTPS - 400KV - Bus 2 | grid_india_gd/grid_events/2026-02-01
G00132 | 2026-02 | 11 | GD-1 | Rajasthan | RJ | Northern | 2026-02-24T10:19 | 2026-02-24T11:51 | 1.53 | 240 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vii)As per PMU at Nokhra(NT), solar generation loss of approx 240 MW occurred at Nokhra(NT) S/s. | 11 GD-1 Rajasthan 24-02-2026 10:19 24-02-2026 11:51 01:32 240 0 0.38% 0.00% 62390 65557 i)Generation of 220kV Nokhra (NT) stations evacuates through 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt which is further connected to 220/33kV 100 MVA ICT-1, 2 & 3 at Nokhra(NT). ii)During antecedent condition, 220kV Nokhra (NT) was generating approx 240 MW (as per PMU). iii)As reported, at 10:19hrs, Y-ph VCB (Vacuum Circuit Breaker) of Capacitor bank bay-1 at Nokhra(NT) was burst. iv)Due to this, 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt tripped on Y-N phase to earth fault; fault sensed in zone-1 at Nokhra(NT) end (exact nature and location of fault yet to be shared). As per PMU, fault current of approx 842.38 A was observed at Nokhra(NT) end. v)During the same time, 220/33kV 100 MVA ICT-1, 2 & 3 at Nokhra(NT) also tripped due to loss of evacuation path which led to complete blackout of 220kV Nokhra(NT) S/s. vi)As per PMU at Bhadla2(PG), Y-N phase to earth fault was observed with fault clearing time of 80 ms. vii)As per PMU at Nokhra(NT), solar generation loss of approx 240 MW occurred at Nokhra(NT) S/s. 1) 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt 2) 220/33kV 100 MVA ICT-1 at Nokhra(NT) 3) 220/33kV 100 MVA ICT-2 at Nokhra(NT) 4) 220/33kV 100 MVA ICT-3 at Nokhra(NT) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load | grid_india_gd/grid_events/2026-02-01
G00133 | 2026-02 | 30 | GD-1 | WB |  |  | 2026-02-24T17:36 | 2026-02-24T17:40 | 0.07 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 2 GD-1 WB 24-02-2026 17:36 24-02-2026 17:40 00:04 Hrs 0 250 0.00% 1.11% 32126 22515 Prior to the disturbance 400kV Malda-New Purnea line-1 was under planned shutdown and bus bar protection was out of service due to CRP upgradation work at Malda. At 17:36 Hrs, during charging of 400kV-Malda-New Purnea line-1, bus fault was occurred at 400kV Malda S/s due to pantograph type isolator which led to tripping of all emanating line in Z-4 protection. 400/220/132kV Malda S/s became dead and load loss of 250 MW was reported at radially connected Gazole and Malda(WB) S/s. 400KV MAIN BUS - 1 AT MALDA(PG) 400KV MAIN BUS - 2 AT MALDA(PG) 400KV-FSTPP-MALDA(PG)-2 400KV-FSTPP-MALDA(PG)-1 400KV-MALDA(PG)-NEW PURNEA-2 220KV-Malda (PG)-GAZOLE-2 220KV-Malda (PG)-GAZOLE-1 220KV MAIN BUS - 1 AT MALDA(PG) 220KV MAIN BUS - 2 AT MALDA(PG) 132KV MAIN BUS - 1 AT MALDA(PG) 132KV MAIN BUS - 2 AT MALDA(PG) 400KV/220KV 500 MVA ICT 3 AT MALDA 400KV/220KV 500 MVA ICT 5 AT MALDA(PG) 220KV/132KV 160 MVA ICT 1 AT MALDA 220KV/132KV 160 MVA ICT 2 AT MALDA Elements Tripped Details of Grid Events during the Month of February 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fa | grid_india_gd/grid_events/2026-02-01
G00134 | 2026-02 | 28 | GI-2 | Andhra Pradesh | AP | Southern | 2026-02-25T16:03 | 2026-02-25T17:24 | 1.35 | 420 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | This led to the tripping of Unit-2 and generation loss of around 420MW. | 13 GI-2 ANDHRA PRADESH 25-02-2026 16:03 25-02-2026 17:24 01:21 420 0 0.01 % 0.0 % 50024.01 65083.8 Tripping of 400kV Bus-1 and 2 at Simhadri TPS of NTPC The triggering incident is the R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-4 main bay leading to BBP operation and tripping of all the main breakers connected to Bus-2 and 400KV-SIMHADRI-KALPAKKA-4. Subsequently, after around 5s, Bus-1 BBP operated due to R-ph CT tracking in 400KV-SIMHADRI-KALPAKKA-3 main bay leading to tripping of all elements connected to 400kV Bus-1 and 2 at Simhadri TPS of NTPC. This led to the tripping of Unit-2 and generation loss of around 420MW. During the event, 400kV Bus-3 and 4 were in service at Simhadri TPS 400KV-SIMHADRI-VEMAGIRI_AP-1, 400KV/11KV SIMHADRI- ST-3, 400KV-SIMHADRI-KALPAKKA-3, 400KV-SIMHADRI- KALPAKKA-4, 420KV/21KV SIMHADRI-GT-2, SIMHADRI - 400KV - Bus 1, SIMHADRI - 400KV - Bus 2 Details of Grid Events during the Month of February 2026 in Southern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW | grid_india_gd/grid_events/2026-02-01
G00135 | 2026-02 | 12 | GD-1 | Rajasthan | RJ | Northern | 2026-02-26T17:05 | 2026-02-26T19:51 | 2.77 | 105 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vii)As per PMU at Nokhra(NT), solar generation loss of approx 105 MW occurred at Nokhra(NT) S/s. | 12 GD-1 Rajasthan 26-02-2026 17:05 26-02-2026 19:51 02:46 105 0 0.21% 0.00% 50942 52139 i)Generation of 220kV Nokhra (NT) stations evacuates through 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt which is further connected to 220/33kV 100 MVA ICT-1, 2 & 3 at Nokhra(NT). ii)During antecedent condition, 220kV Nokhra (IP) was generating approx 105 MW (as per PMU). iii)As reported, at 17:05hrs, 220/33kV 100 MVA ICT-2 at Nokhra(IP) tripped on R-N phase to earth fault (exact reason, nature and location of fault along with exact nature of protection operation yet to be shared) . iv)During the same time, 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt also tripped (exact reason of tripping and nature of protection operation yet to be shared) sensing the same fault. As per PMU, fault current of approx 1254.5 A was observed at Nokhra(NT) end. v)With tripping of 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt, complete blackout occurred at 220kV Nokhra (NT) S/s due to loss of evacuation path. vi)As per PMU at Bhadla2(PG), R-N phase to earth fault was observed with fault clearing time of 80 ms. vii)As per PMU at Nokhra(NT), solar generation loss of approx 105 MW occurred at Nokhra(NT) S/s. 1) 220/33kV 100 MVA ICT-2 at Nokhra(IP) 2) 220 KV Nokhra SL_BHD2 (NTPC)-Bhadla_2 (PG) (NTPC_NOKHRA) Ckt | grid_india_gd/grid_events/2026-02-01
G00136 | 2026-02 | 13 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-02-27T21:26 | 2026-02-27T22:23 | 0.95 | 40 | 170 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 40 MW occurred at 132kV Sewa-2(NH). | 13 GD-1 Jammu and Kashmir 27-02-2026 21:26 27-02-2026 22:23 00:57 40 170 0.09% 0.34% 42524 50371 i)During antecedent condition, only 40 MW unit-1 at Sewa-2(NH) was in running condition and was generating approx 40 MW . ii)As reported, at 21:26 hrs, R-ph CT of 220/132 kV 200 MVA ICT-1 at Hiranagar(JK) got damaged. iii)During the same time, 220 KV Samba(PG)-Hiranagar(PDD) (PG) Ckt-1 & 2 tripped from Hiranagar(JK) end only along with 132 KV Hiranagar(PDD)-Sewa_2(NH) (PG) Ckt-1 & 2 (exact reason of tripping and nature of protection operation yet to be shared). iv)During the same time, as per SCADA data, both the buses at 132kV Sewa-2(NH) tripped and complete blackout occurred at 132kV Sewa-2(NH) (exact reason of busbar tripping yet to be shared). v)As per PMU at Samba(PG), R-N phase to earth fault is observed with delayed fault clearing time of 960ms. vi)As per SCADA, change in demand of approx 170 MW is observed in J&K control area. vii)As per SCADA, generation loss of approx 40 MW occurred at 132kV Sewa-2(NH). 1) 220 KV Samba(PG)-Hiranagar(PDD) (PG) Ckt-1 2) 220 KV Samba(PG)-Hiranagar(PDD) (PG) Ckt-2 3) 132 KV Hiranagar(PDD)-Sewa_2(NH) (PG) Ckt-1 4) 132 KV Hiranagar(PDD)-Sewa_2(NH) (PG) Ckt-2 | grid_india_gd/grid_events/2026-02-01
G00137 | 2026-02 | 14 | GD-1 | Uttar Pradesh | UP | Northern | 2026-02-28T15:30 | 2026-02-28T15:54 | 0.4 | 0 | 228 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 400 KV Azamgarh-Gorakhpur (UP) Ckt 2) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-1 3) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-2 4) 400/220 kV 500 MVA ICT 1 at Gorakhpur(UP) 5) 400/220 kV 500 MVA ICT 2 at Gorakhpur(UP) 6) 400/220 kV 315 MVA ICT 3 at Gorakhpur(UP) 7) 400kV Bus-1 at Gorakhpur(UP) 8) 400kV Bus-2 at Gorakhpur(UP) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Lo | 14 GD-1 Uttar Pradesh 28-02-2026 15:30 28-02-2026 15:54 00:24 0 228 0.00% 0.41% 55222 55237 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)As reported, at 15:30 hrs, B-ph disc insulator of 400kV Bus-1 at Gorakhpur(UP) was burst out. iii)As per DR, on this fault, bus bar protection operated (both zone-1 and zone-2) in both the buses of 400kV Gorakhpur(UP). iv)All the elements connected to both 400kV buses tripped and complete blackout occurred at 400/220kV Gorakhpur(UP). v)As per at Lucknow(PG), B-N phase to earth fault was observed with fault clearing time of 80 ms. vi)As per SCADA, change in demand of approx 170 MW was observed in UP control area. However, as reported by SLDC UP , load loss of approx 228 MW occurred in UP control area. 1) 400 KV Azamgarh-Gorakhpur (UP) Ckt 2) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-1 3) 400 KV Gorakhpur(PG)-Gorakhpur(UP) (PG) Ckt-2 4) 400/220 kV 500 MVA ICT 1 at Gorakhpur(UP) 5) 400/220 kV 500 MVA ICT 2 at Gorakhpur(UP) 6) 400/220 kV 315 MVA ICT 3 at Gorakhpur(UP) 7) 400kV Bus-1 at Gorakhpur(UP) 8) 400kV Bus-2 at Gorakhpur(UP) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-02-01
G00138 | 2026-03 | 25 | GD-1 | Gujarat | GJ | Western | 2026-03-01T10:57 | 2026-03-01T15:44 | 4.78 |  |  | FALSE | TRUE | FALSE | FALSE | TRUE | At the time of event, no generation was present at Gadhsisa Wind Power Plant (Renew Power). | 1 GD-1 Gujarat 01-03-2026 10:57 01-03-2026 15:44 04:47 - - - - 70283 60242 Complete outage of 220 kV Gadhsisa (Renew Power):At 10:57 hrs / 01-03-2026, 220 kV Bhuj-Gadhsisa-1 S/C tripped on B-E fault. At Bhuj end, it is observed from disturbance recorders that three phase trip issued for a single phase fault and DT sent to Gadhsisa end. During patrolling, tree infringement was found between tower number 46C/0 to 46/B. Earlier the line was charged on 25-02-2026 after attending tower (Tower no. 46C/1) collapse due to conductor theft attempt indicating that Tree infringement was not completely addressed during this period. At the time of event, no generation was present at Gadhsisa Wind Power Plant (Renew Power). 1. 220 kV Bhuj-Gadhsisa-1 S/C | grid_india_gd/grid_events/2026-03-01
G00139 | 2026-03 | 1 | GI-2 | Rajasthan | RJ | Northern | 2026-03-02T14:50 | 2026-03-02T15:51 | 1.02 | 0 | 375 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-2 Rajasthan 02-03-2026 14:50 02-03-2026 15:51 01:01 0 375 0.00% 0.73% 56682 51512 i)400/220kV Ajmer(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)As reported, at 12:42 hrs, 400 KV Ajmer(RS)-Deedwana(MTS) (RS) Ckt auto-reclosed from | 1 GI-2 Rajasthan 02-03-2026 14:50 02-03-2026 15:51 01:01 0 375 0.00% 0.73% 56682 51512 i)400/220kV Ajmer(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)As reported, at 12:42 hrs, 400 KV Ajmer(RS)-Deedwana(MTS) (RS) Ckt auto-reclosed from both the ends on transient fault. iii)Further, at 14:50 hrs, 400 KV Ajmer(RS)-Deedwana(MTS) (RS) Ckt tripped on R-N phase to earth fault with fault distance of 14.69km from Ajmer(RS) end and 84.9km from Deedwana end. During patrolling, some burnt bushes were found between Tower No. 38-39 and same were cleared from line range. iv)As per DR at Ajmer(RS) end of 400 KV Ajmer(RS)-Deedwana(MTS) (RS) Ckt, B-N Phase to earth fault (phase sequence issue at Ajmer(RS)) with unsuccessful A/R was observed with fault current of ~11.06 kA from Ajmer(RS) end. Delayed fault clearing time=~1.5 sec. Zone-1 distance protection operated at Ajmer(RS) end. v)During the same time, 400 KV Ajmer(RS)-Ajmer(PG) (PG) Ckt-1 & 2 also tripped sensing this fault (delayed clearance) in zone-3 at Ajmer(PG) end. vi)As per DR, 400 KV Phagi-Ajmer (RS) Ckt-1 tripped on over-voltage stage-1 operation at Phagi(RS) end (Voltage reached 1.11 pu at Phagi end) and 400 KV Phagi-Ajmer (RS) Ckt-2 tripped sensing this fault (delayed clearance) in zone-3 at Phagi(RS) end (Fault current, Ir=~1.374kA from Phagi end). vii)Due to delayed clearance of fault, 400/220 kV 315 MVA ICT 1 & 3 at Ajmer(RS) also tripped on O/C E/F (51N) and D | grid_india_gd/grid_events/2026-03-01
G00140 | 2026-03 | 26 | GD-1 | Gujarat | GJ | Western | 2026-03-02T23:05 | 2026-03-02T23:36 | 0.52 | 86 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss of 69 MW at Gadhsisa SS & 17 MW at Baranda SS generation loss reported. | 2 GD-1 Gujarat 02-03-2026 23:05 02-03-2026 23:36 00:31 86 - 0.12% - 71012 62932 Complete outage of 220 kV Baranda (Avikiran) & 220kV Gadhsisa (Renew) At 23:05 hrs/ 02-03-26, 220kV Bhuj–Baranda line tripped due to Y-B phase-phase fault. At the same time, 220kV Bhuj-Gadhsisa line tripped due to relay mal-operation at Gadhsisa end. Due to loss of evacuation path, 220kV Baranda & Gadhsisa RE stations became dead. As reported by Avikiran- Baranda, a foreign conducting object was found on line probably act of miscreants. Generation loss of 69 MW at Gadhsisa SS & 17 MW at Baranda SS generation loss reported. 1. 220kV Bhuj Gadhsisa S/C 2. 220kV Bhuj Baranda S/C 3. 220/33 kV 150 MVA Baranda ICT-1 4. 220/33 kV 150 MVA Baranda ICT-2 5. 220/33 kV 160 MVA Gadhsisa ICT-1 6. 220/33 kV 160 MVA Gadhsisa ICT-2 | grid_india_gd/grid_events/2026-03-01
G00141 | 2026-03 | 2 | GI-1 | Rajasthan | RJ | Northern | 2026-03-04T01:44 | 2026-03-04T04:01 | 2.28 | 362 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 362 MW was observed at KTPS(RS). | 2 GI-1 Rajasthan 04-03-2026 01:44 04-03-2026 04:01 02:17 362 0 0.99% 0.00% 36442 38356 i)220kV KTPS(RS) has 6 buses at 220kV level. Bus 3 and Bus 5 are connected through an isolator. Bus 2 and Bus 4 are connected without any isolator or bus coupler. Bus 1 is connected to Bus 3 via a bus sectionalizer, Bus 3 is connected to Bus 4 via a bus coupler and Bus 5 is connected to Bus 6 via a bus coupler. ii)During antecedent condition, 220 KV Ranpur-KTPS (RS) Ckt-1, 220 KV Kota Sakatpura-KTPS (RS) Ckt-3 & 210 MW Kota TPS - UNIT 5 were connected to 220 kV Bus-3 at KTPS(RS) and 220 KV Kota(PG)-KTPS(RVUN) (RS) Ckt-1 & 195 MW Kota TPS - UNIT 7 were connected to 220 kV Bus-5 at KTPS(RS). As per SCADA, 210 MW Kota TPS - UNIT 5 and 195 MW Kota TPS - UNIT 7 were generating approx 172 MW and 190 MW respectively. iii)As reported, at 01:44 hrs, 220 KV Kota(PG)-KTPS(RVUN) (RS) Ckt-1 tripped on B-N phase to earth fault with fault distance of 6.5 km and fault current of 5.037 kA from Kota(PG) end. As per DR, (Zone-2 Start + Carrier received) at Kota(PG) end. iv)Due to some problem in the line CB at KTPS end of 220 KV Kota(PG)-KTPS(RVUN) (RS) Ckt-1, LBB operated at KTPS(RS) resulting in the tripping of 220 kV Bus-3 & 5 at KTPS(RS). As per DR, voltage became zero after 200 ms of opening of CB at Kota(PG) end ensuring LBB operation at KTPS end. v)This led to tripping of all the elements connected to 220 kV Bus-3 & 5 at KTPS(RS) and both the buses became dead. vi)As per PMU at KTPS(RS), B-N phase to e | grid_india_gd/grid_events/2026-03-01
G00142 | 2026-03 | 27 | GD-1 | DNH |  |  | 2026-03-04T18:28 | 2026-03-04T19:13 | 0.75 |  | 192 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GD-1 DNH 04-03-2026 18:28 04-03-2026 19:13 00:45 - 192 - 0.33% 67563 57977 Complete outage of 220/66 kV Kharadpada S/S (DNH): At 18:28 hrs, 220kV Kharadpada S/s 220/66kV 160MVA ICT-1 and 100MVA ICT-2 tripped on 220 kV Bus-1 bus bar protection operation due to R phase CT burst of 100MVA ICT-2. At t | 3 GD-1 DNH 04-03-2026 18:28 04-03-2026 19:13 00:45 - 192 - 0.33% 67563 57977 Complete outage of 220/66 kV Kharadpada S/S (DNH): At 18:28 hrs, 220kV Kharadpada S/s 220/66kV 160MVA ICT-1 and 100MVA ICT-2 tripped on 220 kV Bus-1 bus bar protection operation due to R phase CT burst of 100MVA ICT-2. At that time, 220kV Ambheti–Kharadpada, 220kV Ambheti–Bhilosa, 220kV Bhilosa–Kharadpada, and 220kV Kharadpada–New Kharadpada Ckt-1 & 2 tripped due to operation of busbar protection. At that time, 160MVA ICT-4, 100MVA ICT-3, and 220kV TRF/Bus-II were under emergency shutdown. 220 kV Vapi-Bhilosa also tripped on recipt of DT at Vapi which is undesirable. Due to the event, 220kV Kharadpada Substation and 220kV Bhilosa Switching Station became dead (blackout condition). The total load loss was approximately 192 MW at Kharadpada and Bhilosa. 1. 220/66 KV 160 MVA ICT -1 2. 220/66 KV 100 MVA ICT -2 3. 220kV Kharadpada-New Kharadpada ckt-1 4. 220kVapi-Bhilosa ckt 5. 220Kv Kharadpada- Vapi ckt 6. 220Kv Kharadpada-Bhilosa ckt 7. 220/66 KV 100 MVA Tr. -3[HV] 8. 220/66 KV 160 MVA Tr. -4[HV] | grid_india_gd/grid_events/2026-03-01
G00143 | 2026-03 | 28 | GI-2 | Maharashtra | MH | Western | 2026-03-05T11:27 | 2026-03-05T14:15 | 2.8 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Maharashtra 05-03-2026 11:27 05-03-2026 14:15 02:48 - - - - 83379 70794 Partial outage of 400/220 kV Aurangabad (Waluj) (MSETCL):At 11:27 hrs / 05-03-2026, B-phase suspension insulator string of the 400 kV Aurangabad(MH)-Transfer Bus burst, triggering the 400 kV Aurangabad(MH)-Bus-1 busbar pr | 4 GI-2 Maharashtra 05-03-2026 11:27 05-03-2026 14:15 02:48 - - - - 83379 70794 Partial outage of 400/220 kV Aurangabad (Waluj) (MSETCL):At 11:27 hrs / 05-03-2026, B-phase suspension insulator string of the 400 kV Aurangabad(MH)-Transfer Bus burst, triggering the 400 kV Aurangabad(MH)-Bus-1 busbar protection (Double Main and Transfer bus scheme), leading to the tripping of all elements connected to Bus- 1. As reported by Maharashtra 400 kV Aurangabad(MH)-Deepnagar-1 S/C was being shifted to the 400 kV Transfer Bus to facilitate timing testing for the Deepnagar circuit breaker. The 400 kV Transfer bus was charged via the 89C isolator of the 400 kV Deepnagar bay. Immediately upon charging, the B-phase suspension insulator string of the 400 kV Transfer bus around 400 kV Aurangabad(MH)-Pune-2 and 400 kV Aurangabad(MH)- Aurangabad(PG)-2 bay burst. No generation or load loss occurred during the event as 400 kV Aurangabad(MH)-Bus-2 was intact. 1. 400 kV Aurangabad(MH)-Bus-1 2. 400 kV Aurangabad(MH)-Deepnagar-1 S/C 3. 400 kV Aurangabad(MH)- Aurangabad(PG)-2 4. 400 kV Aurangabad(MH)-Pune-2 5. 400/220 kV Aurangabad(MH)-ICT-3 (500 MVA) | grid_india_gd/grid_events/2026-03-01
G00144 | 2026-03 | 29 | GI-1 | Gujarat | GJ | Western | 2026-03-05T13:10 | 2026-03-05T20:50 | 7.67 |  |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 74 MW occurred at Baranda(Avikiran) Wind Power Plant due to loss of evacuation path. | 5 GI-1 Gujarat 05-03-2026 13:10 05-03-2026 20:50 07:40 - - - - 76339 65889 Partial outage of 220 kV Baranda (Avikiran):At 13:10 hrs / 05-03-2026, 220/33 kV Baranda-ICT-1&2 tripped on Over flux protection. The cause of the transformer tripping was opening of the B-phase jumper at Tower No. 101 on the 220 kV Bhuj-Baranda-1 S/C. This open-phase condition caused a severe voltage unbalance as seen in PMU Voltage plot of 220 kV Bhuj-Baranda-1 S/C. (The B-phase voltage (Vb) recorded a temporary apparent rise to 145.6 kV, which is approximately 1.146 per unit (pu) compared to the rated 127 kV phase-to-neutral voltage). This triggered a severe single-phasing condition and subsequent neutral displacement. It was not a genuine, sustained system-wide transformer over-flux condition or an internal transformer fault. Generation loss of 74 MW occurred at Baranda(Avikiran) Wind Power Plant due to loss of evacuation path. 1. 220/33 kV Baranda-ICT-1 2. 220/33 kV Baranda-ICT-2 | grid_india_gd/grid_events/2026-03-01
G00145 | 2026-03 | 30 | GD-1 | Goa | GA | Western | 2026-03-06T17:32 | 2026-03-06T18:07 | 0.58 |  | 479 | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GD-1 Goa 06-03-2026 17:32 06-03-2026 18:07 00:35 - 479 - 0.66% 84315 72149 Complete outage of 400 kV Mapusa S/S:1. At 17:32 Hrs/ 06-03-2026, at 400/220 kV Mapusa S/S ( DMT scheme at 220 kV level), a 220 kV bus fault occurred due to the intrusion of foreign material i.e., a bird—that entered the in | 6 GD-1 Goa 06-03-2026 17:32 06-03-2026 18:07 00:35 - 479 - 0.66% 84315 72149 Complete outage of 400 kV Mapusa S/S:1. At 17:32 Hrs/ 06-03-2026, at 400/220 kV Mapusa S/S ( DMT scheme at 220 kV level), a 220 kV bus fault occurred due to the intrusion of foreign material i.e., a bird—that entered the induction zone of bay 203–89A of the 220 kV Amona feeder, leading to a fault on 220 kV Bus #2. 220 kV Bus-1 was under planned shutdown for AMP works prior to the event. Due to faulty CT supervision relay, busbar protection was in blocked condition prior to event. The fault was cleared by tripping of 400/220 kV ICTs on Backup overcurrent protection operation at Mapusa. All 220 kV lines to Mapusa tripped from remote ends on zone-2/3. 400 kV Mapusa-Kolhapur-1 and 400 kV Mapusa-Xeldem-2 tripped after 5 seconds of load throw off on stage-1 overvoltage. 400 kV Xeldem-1 and 400 kV Kolhapur-2 went floating since 220 kV load feeding lines were tripped. At the same time, 220 kV Xeldem(Sterlite)- Xeldem-2, 220 kV Xeldem(Sterlite)- Xeldem 1 (idle charged from Sterlite end) tripped on Over Voltage protection operation at Xeldem (Sterlite end). 220 kV Tivim S/S went dark & partial load connected at 220 kV Xeldem & 220 kV Ponda got affected due to spilt bus operation. Load loss of 479 MW reported by Goa. 1. 220 kV Mapusa Bus 2 2. 400/220 kV 315 MVA Mapusa ICT 1 3. 400/220 kV Mapusa 315 MVA ICT 2 4. 400/220 kV 315 MVA Mapusa ICT 3 5. 400 kV Kolhapur- Mapusa 1 6. 400 kV Mapusa- Xeldem-2 7. 220 kV Xel | grid_india_gd/grid_events/2026-03-01
G00146 | 2026-03 | 3 | GI-1 | Rajasthan | RJ | Northern | 2026-03-07T13:23 | 2026-03-07T13:47 | 0.4 | 334 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per SCADA, at 13:23 hrs, generation loss of approx 124 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 210 MW was observed. | 3 GI-1 Rajasthan 07-03-2026 13:23 07-03-2026 13:47 00:24 334 0 0.58% 0.00% 57929 56300 i)220kV Barsingsar(NLC) has double main and transfer bus scheme at 220kV level. ii)During antecedent condition, 125 MW Barsingsar(NLC) - Unit 1 & 2 were generating approx 122 MW and 124 MW respectively. iii)As reported, at 13:23 hrs, 220 kV Barsingsar(NLC)-Nagaur (RS) Ckt tripped on Y-B phase to phase fault (as per PMU) with fault distance of 25 km from Nagaur end; fault sensed in zone-1 at Nagaur end. iv)During the same time, 220 kV Barsingsar-Bikaner ckt and 125 MW Barsingsar(NLC) - Unit 2 also tripped (exact reason of tripping along with nature of protection operation yet to be shared). v)As per PMU at Kota(PG), Y-B phase to phase fault was observed with fault clearing time of 120 ms. vi)As per SCADA, at 13:23 hrs, generation loss of approx 124 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 210 MW was observed. 1) 220 kV Barsingsar(NLC)-Nagaur (RS) Ckt 2) 220 kV Barsingsar(NLC)-Bikaner Ckt 3) 125 MW Barsingsar(NLC) - Unit 2 | grid_india_gd/grid_events/2026-03-01
G00147 | 2026-03 | 4 | GD-1 | Rajasthan | RJ | Northern | 2026-03-07T13:34 | 2026-03-07T13:45 | 0.18 | 392 | 70 | TRUE | FALSE | FALSE | FALSE | TRUE | v)As per SCADA, at 13:34 hrs, generation loss of approx 122 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 270 MW & change in demand of approx 70 MW were observed in Rajasthan control area. | 4 GD-1 Rajasthan 07-03-2026 13:34 07-03-2026 13:45 00:11 392 70 0.69% 0.12% 57083 56782 i)Further, at 13:34 hrs, 220 kV Barsingsar-Khinwsar ckt, 220 kV Barsingsar-Baap ckt and 125 MW Barsingsar(NLC) - Unit 1 tripped (exact reason of tripping along with nature of protection operation yet to be shared). ii)As per SCADA SOE, 220 kV Baap-Phalodi(RS) ckt also tripped during the same time (exact reason of tripping along with nature of protection operation yet to be shared). iii)Due to this, complete blackout occurred at 220 kV Barsingsar(NLC) and 220/132/33kV Baap(RS) S/s. iv)As per PMU at Kota(PG), no fault was observed in the system. v)As per SCADA, at 13:34 hrs, generation loss of approx 122 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 270 MW & change in demand of approx 70 MW were observed in Rajasthan control area. 1) 220 kV Barsingsar(NLC)-Khinwsar (RS) Ckt 2) 220 kV Barsingsar(NLC)-Baap (RS) Ckt 3) 125 MW Barsingsar(NLC) - Unit 1 | grid_india_gd/grid_events/2026-03-01
G00148 | 2026-03 | 5 | GD-1 | Rajasthan | RJ | Northern | 2026-03-07T14:01 | 2026-03-07T15:34 | 1.55 | 104 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per PMU and SCADA, solar generation loss of approx 104 MW was observed at 220kV Juniper Green(JGCPL)(IP). | 5 GD-1 Rajasthan 07-03-2026 14:01 07-03-2026 15:34 01:33 104 0 0.18% 0.00% 58416 57852 i)Generation of 220kV Juniper Green(JGCPL)(IP) station evacuates through 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt. ii)During antecedent condition, 220kV Juniper Green(JGCPL)(IP) station was generating approx 104 MW (as per PMU and SCADA). iii)As reported, at 14:01 hrs, 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt tripped on B-ph line differential protection operation at JGCPL end (exact reason, nature and location of fault yet to be shared). iv)Due to tripping of 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt, complete blackout occurred at 220kV Juniper Green(JGCPL)(IP) due to loss of evacuation path. v)As per PMU at Bikaner-2(PG), B-N phase to earth fault was observed with fault clearing time of 80 ms. vi)As per PMU and SCADA, solar generation loss of approx 104 MW was observed at 220kV Juniper Green(JGCPL)(IP). 1) 220 KV Bikaner_2 (PBTSL)-JGCPL_SL_BIK2_PG (Juniper_NEPL) Ckt | grid_india_gd/grid_events/2026-03-01
G00149 | 2026-03 | 6 | GD-1 | Haryana | HR | Northern | 2026-03-07T20:08 | 2026-03-07T22:22 | 2.23 | 0 | 450 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 6 GD-1 Haryana 07-03-2026 20:08 07-03-2026 22:22 02:14 0 450 0.00% 0.78% 50189 58053 i)220/132kV Mohana(HV) has double main bus scheme at 220kV level. ii)During antecedent condition, 220 KV Mohana(HV)-Sonipat(PG) (HVPNL) Ckt-1, 2, 3 & 4 were connected to 220kV Bus-1 at Mohana(HV) and 220 KV Mohana(HV)- Sampla (HVPNL) Ckt-1 & 2 and 220/132kV 100 MVA ICT-2 at Mohana(HV) were connected to 220kV Bus-2 at Mohana(HV). iii)As reported, at 20:08 hrs, B-Ph CT of 220/132kV 100 MVA ICT-2 at Mohana(HV) burst occurred. iv)During the same time, 220 KV Mohana(HV)-Sonipat(PG) (HVPNL) Ckt-1, 2, 3 & 4 also tripped from Sonipat(PG) end only. As per DR, fault sensed in zone-2 (delayed fault clearance of ~400ms) for 220 KV Mohana(HV)-Sonipat(PG) (HVPNL) Ckt-1 & 2 and in zone-3 (delayed fault clearance of ~840ms) for 220 KV Mohana(HV)- Sonipat(PG) (HVPNL) Ckt-3 & 4 from Sonipat(PG) end. v)As per SCADA SOE, 220 KV Sonipat(PG)- IMT Kharkhoda A (HVPNL) Ckt-1 and 220 KV Mohana(HV)-Sampla (HVPNL) Ckt-1 & 2 also tripped during the same time (exact reason of tripping and nature of protection operation yet to be shared). vi)Due to tripping of all the 220kV lines from Mohana(HV), complete blackout occurred at 220/132kV Mohana(HV) S/s. vii)As per PMU at Sonipat(PG), B-N fault followed by B-N fault converted to Y-B-N fault was observed with fault clearing time of 80 ms and 840 ms (delayed) respectively. viii)As per SCADA, change in demand of approx 450 MW was observed in Haryana control area. 1) 220 KV Mohan | grid_india_gd/grid_events/2026-03-01
G00150 | 2026-03 | 7 | GI-2 | Rajasthan | RJ | Northern | 2026-03-09T14:37 | 2026-03-09T17:46 | 3.15 | 162 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 162 MW was observed at Chhabra TPS(RS). | 7 GI-2 Rajasthan 09-03-2026 14:37 09-03-2026 17:46 03:09 162 0 0.27% 0.00% 59321 59366 i)During antecedent condition, 400 kV Bhilwara (RS) – Chhabra (RVUN) Ckt-1 was already under planned shutdown since 11:29 hrs. 250 MW Chhabra Unit-1, 2, 3 & 4 were running and generating approx 154 MW, 145 MW, 144 MW and 162 MW respectively (as per SCADA). ii)As reported, at 14:37 hrs, 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) Ckt-1 tripped on R-N Phase to earth fault with fault distance of 269.7 km from Hindaun end and 27.4 km from Chhabra TPS end. iii)As per DR, fault current was 1.268 kA from Hindaun end and 8.896 kA from Chhabra TPS end; fault sensed in zone-1 at Chhabra end and in zone-2 at Hindaun end. iv) As reported by SLDC Rajasthan, in case of N-1-1/N-2 contingency of 400 kV Chhabra-Hindaun & Chhabra-Bhilwara, if total generation at Chhabra TPS is >550 MW but <750 MW, then only one unit of Chhabra TPS will trip and if total generation at Chhabra TPS is >750 MW, then two units of Chhabra TPS will trip. v)Due to tripping of 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) Ckt-1 with 400 kV Bhilwara (RS) – Chhabra (RVUN) Ckt-1 under outage, 250 MW Chhabra Unit-4 tripped on SPS operation as per SPS logic related to Safe evacuation of generation of Chhabra TPS (Case-3). vi)As per PMU at Bassi(PG), R-N Phase to earth fault with unsuccessful A/R was observed with fault clearing time of 80 ms. vii)As per SCADA, generation loss of approx 162 MW was observed at Chhabra TPS(RS). 1) 400 KV Hindaun(RS)-Chhab | grid_india_gd/grid_events/2026-03-01
G00151 | 2026-03 | 12 | GD-1 | Punjab | PB | Northern | 2026-03-10T10:39 | 2026-03-10T10:54 | 0.25 | 0 | 10 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GD-1 Punjab 10-03-2026 10:39 10-03-2026 10:54 00:15 0 10 0.00% 0.02% 58799 62079 i)220/66KV Mehal Kalan(PS) has double main bus scheme at 220kV level. ii)As reported, at 10:39 hrs, B-ph CT of 220 KV Moga(PG)-Mehal Kalan(PS) (PSTCL) Ckt-2 blast occured which further led to bus bar protection opera | 12 GD-1 Punjab 10-03-2026 10:39 10-03-2026 10:54 00:15 0 10 0.00% 0.02% 58799 62079 i)220/66KV Mehal Kalan(PS) has double main bus scheme at 220kV level. ii)As reported, at 10:39 hrs, B-ph CT of 220 KV Moga(PG)-Mehal Kalan(PS) (PSTCL) Ckt-2 blast occured which further led to bus bar protection operation at Mehal Kalan(PS). iii)Due to busbar operation, all the elements connected to 220kV Bus-1 & 2 at Mehal Kalan(PS) tripped and complete blackout occurred at 220/66KV Mehal Kalan(PS). iv)As per PMU at Jalandhar(PG), B-N phase to earth fault is observed with fault clearing time of 560 ms. v)As per SCADA, change in demand of approx 10 MW is observed in Punjab control area. 1) 220 KV Moga(PG)-Mehal Kalan(PS) (PSTCL) Ckt-1 2) 220 KV Moga(PG)-Mehal Kalan(PS) (PSTCL) Ckt-2 3) 220 kV Pakhwal-Mehal Kalan (PS)(PSTCL) CKT-1 4) 220 kV Pakhwal-Mehal Kalan (PS)(PSTCL) CKT-2 5) 220kV Bus-1 at Mehal Kalan(PS) 6) 220kV Bus-2 at Mehal Kalan(PS) 7) 220/66kV 100MVA ICT 1 at Mehal Kalan(PS) 8) 220/66kV 100MVA ICT 2 at Mehal Kalan(PS) | grid_india_gd/grid_events/2026-03-01
G00152 | 2026-03 | 8 | GD-1 | Rajasthan | RJ | Northern | 2026-03-10T12:47 | 2026-03-10T15:05 | 2.3 | 249 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | , ~249 MW lost due to loss of evacuation path. | 8 GD-1 Rajasthan 10-03-2026 12:47 10-03-2026 15:05 02:18 249 0 0.42% 0.00% 58828 59099 i)220kV ACME Solar RE station connected at Bhadla(PG) at 220kV level and its generation evacuates through 220kV Bhadla(PG)-ACME Solar(IP) line. During antecedent condition, 220kV ACME RE station was generating ~249MW. ii)As reported at 12:47 hrs, 220 KV BHADLA(PG)-ACME Solar(ACME) line tripped on R-N phase to earth fault. Fault occurred due to snapping of R-Ph Jumper. iii)Due to tripping of line, complete generation of ACME Solar i.e., ~249 MW lost due to loss of evacuation path. iv)As per PMU at Bhadla(PG), voltage dip in R & B phase is observed. v)As per DR of Bhadla(PG) end of the line, R-N fault with fault current of ~14.1 kA and 3-ph trip without A/R operation is observed. vi)As per SCADA, change in NR solar generation of ~200 MW is observed. 1) 220 KV Bhadla(PG)-ACME Solar(ACM) (ACME) Ckt-1 | grid_india_gd/grid_events/2026-03-01
G00153 | 2026-03 | 11 | GI-2 | Rajasthan | RJ | Northern | 2026-03-10T13:55 | 2026-03-10T17:22 | 3.45 | 180 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 180 MW was observed at Chhabra TPS(RS). | 11 GI-2 Rajasthan 10-03-2026 13:55 10-03-2026 17:22 03:27 180 0 0.31% 0.00% 58544 57680 i)During antecedent condition, 400 kV Bhilwara (RS) – Chhabra (RVUN) Ckt-1 was already under planned shutdown. 250 MW Chhabra Unit-1, 2, 3 & 4 were running and generating approx 159 MW, 148 MW, 154 MW and 180 MW respectively (as per SCADA). ii)As reported, at 13:55 hrs, 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) Ckt-1 tripped on R-N Phase to earth fault with fault distance of 271.1 km from Hindaun end and 26.3 km from Chhabra TPS end. iii)As per DR, fault current was 1.312 kA from Hindaun end and 8.985 kA from Chhabra TPS end; fault sensed in zone-1 at Chhabra end and in zone-2 at Hindaun end. iv) As reported by SLDC Rajasthan, in case of N-1-1/N-2 contingency of 400 kV Chhabra-Hindaun & Chhabra-Bhilwara, if total generation at Chhabra TPS is >550 MW but <750 MW, then only one unit of Chhabra TPS will trip and if total generation at Chhabra TPS is >750 MW, then two units of Chhabra TPS will trip. v)Due to tripping of 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) Ckt-1 with 400 kV Bhilwara (RS) – Chhabra (RVUN) Ckt-1 under outage, 250 MW Chhabra Unit-4 tripped on SPS operation as per SPS logic related to Safe evacuation of generation of Chhabra TPS (Case-3). vi)As per PMU at Bassi(PG), R-N Phase to earth fault with unsuccessful A/R was observed with fault clearing time of 80 ms. vii)As per SCADA, generation loss of approx 180 MW was observed at Chhabra TPS(RS). 1) 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) C | grid_india_gd/grid_events/2026-03-01
G00154 | 2026-03 | 10 | GD-1 | Rajasthan | RJ | Northern | 2026-03-10T14:44 | 2026-03-10T15:00 | 0.27 | 0 | 400 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Rajasthan 10-03-2026 14:44 10-03-2026 15:00 00:16 0 400 0.00% 0.68% 60018 58961 i)During antecedent condition, 400/220 kV 315 MVA ICT 1 & 3 at Ajmer(RS) were carrying approx 217 MW and 226 MW respectively. ii)As reported by SLDC Rajasthan, at 14:44 hrs, 220kV KTPS-Bundi(RS) Ckt-1 & 2 tripped | 10 GD-1 Rajasthan 10-03-2026 14:44 10-03-2026 15:00 00:16 0 400 0.00% 0.68% 60018 58961 i)During antecedent condition, 400/220 kV 315 MVA ICT 1 & 3 at Ajmer(RS) were carrying approx 217 MW and 226 MW respectively. ii)As reported by SLDC Rajasthan, at 14:44 hrs, 220kV KTPS-Bundi(RS) Ckt-1 & 2 tripped on B-N phase to earth fault (exact reason, nature and location of fault yet to be shared). iii)Consequently, 220 KV GSS Bundi(RS) was left with a single power source i.e. 220 KV Gulabpura(RS). 220 KV Gulabpura was being supplied by 220 KV Beawar and 220 KV Jethana, both of which were connected to the 400 KV GSS Ajmer(RS). iv)This led to over-loading of 400/220 kV 315 MVA ICT 1 & 3 at Ajmer(RS) triggering the SPS for Transformers at 400KV Ajmer(RVPNL) substation. v)Due to SPS operation, 220 kV Ajmer-Beawer Ckt, 220 kV Ajmer-Kishangarh Ckt and 220 kV Ajmer-Bherunda Ckt-1 & 2 tripped (as per logic). vi)However, the load from 220 KV GSS Bundi(RS), 220 KV Gulabpura(RS) and 220 KV Jethana along with 220kV GSS Ajmer(RS) continued to persist on both 400/220 kV 315 MVA ICT 1 & 3 at Ajmer(RS) and ultimately both the ICTs tripped on overloading. vii)Complete blackout occurred at 220 kV Kishangarh, 220 kV Bherunda, 220 kV Beawar, 220 KV Bundi(RS), 220 KV Gulabpura(RS) and 220 KV Jethana S/s. viii)As per SCADA SOE, 220/132kV ICT-2 at Ras(RS) also tripped during the same time (exact reason of tripping and nature of protection operation yet to be shared). ix)As per PMU at Ajmer(PG), Two consecut | grid_india_gd/grid_events/2026-03-01
G00155 | 2026-03 | 9 | GD-1 | Rajasthan | RJ | Northern | 2026-03-10T15:37 | 2026-03-10T18:10 | 2.55 | 495 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | , ~495 MW lost due to loss of evacuation path. | 9 GD-1 Rajasthan 10-03-2026 15:37 10-03-2026 18:10 02:33 495 0 0.85% 0.00% 58165 57869 i)400kV AGE25L RE station is connected at Bhadla2(PG) at 400kV level and its generation evacuates through 400kV Bhadla2(PG)-AGE25L(IP) line. During antecedent condition, 400kV AGE25L RE station was generating ~495MW. ii)As reported at 15:37 hrs, 400 KV Bhadla2(PG)-AGE25L line tripped on overvoltage stage-1 protection from Bhadla2(PG) end. DT received at AGE25L end. iii)Due to tripping of line, complete generation of AGE25L i.e., ~495 MW lost due to loss of evacuation path. iv)As per PMU at Bhadla2(PG), voltage dip of ~8kV in all three phases is observed. v)As per SCADA data, antecedent bus voltage at 400kV Bhadla2(PG) and AGE25L was ~415kV which was in safe limit. vi)As per SCADA, change in NR solar generation of ~880 MW (solar generation was in ramping down state) is observed. 1) 400 KV AGE25L SL_BHD2_PG-Bhadla_2 (PG) (AGE25L) Ckt- 1 | grid_india_gd/grid_events/2026-03-01
G00156 | 2026-03 | 13 | GD-1 | Rajasthan | RJ | Northern | 2026-03-11T10:56 | 2026-03-11T12:49 | 1.88 | 227 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | , ~227 MW lost due to loss of evacuation path. | 13 GD-1 Rajasthan 11-03-2026 10:56 11-03-2026 12:49 01:53 227 0 0.37% 0.00% 61239 62684 i)220kV ACME Solar RE station connected at Bhadla(PG) at 220kV level and its generation evacuates through 220kV Bhadla(PG)-ACME Solar(IP) line. During antecedent condition, 220kV ACME RE station was generating ~227MW. ii)As reported at 10:56 hrs, 220 KV BHADLA(PG)-ACME Solar(ACME) line tripped on R-N phase to earth fault. Exact reason of occurrence of fault not received. iii)Due to tripping of line, complete generation of ACME Solar i.e., ~227 MW lost due to loss of evacuation path. iv)As per PMU at Bhadla(PG), voltage dip in R & B phase is observed. v)As per DR of Bhadla(PG) end of the line, R-N fault with fault current of ~16.9 kA and 3-ph trip without A/R operation is observed. As per event logger of Bhadla(PG) end, fault location was ~3.6km from Bhadla(PG) end. vi)As per SCADA, change in NR solar generation of ~235 MW is observed. 1) 220 KV Bhadla(PG)-ACME Solar(ACM) (ACME) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of March 2026 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Gr | grid_india_gd/grid_events/2026-03-01
G00157 | 2026-03 | 14 | GI-2 | Rajasthan | RJ | Northern | 2026-03-11T11:41 | 2026-03-11T12:12 | 0.52 | 405 | 65 | TRUE | FALSE | FALSE | FALSE | TRUE | vii)As per SCADA, change in NR total solar generation and Rajasthan solar generation of approx 405 MW and change in demand of approx 65 MW in Rajasthan control area were observed. | 14 GI-2 Rajasthan 11-03-2026 11:41 11-03-2026 12:12 00:31 405 65 0.67% 0.10% 60085 62000 i)400/220kV Bikaner(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)During antecedent condition, active power loading on 400/220 KV 315 MVA ICT 1 & 2 at Bikaner(RS) were 215 MW and 224 MW respectively from 220kV level to 440kV level and reactive power loading were 139 MVAr and 136 MVAr respectively from 400kV level to 220kV level (as per SCADA). iii)As reported, at 11:41 hrs, there was an immediate surge in generation due to tripping of 220 kV Badnu-Tehandesar Ckt. The generation from 220 kV GSS Badnu was diverted via 220 kV GSS Bikaner(RS) to 400 kV GSS Bikaner(RS) which led to overloading of 400/220 KV 315 MVA ICT 1 & 2 at Bikaner(RS). iv)Due to overloading of ICTs at Bikaner(RS), “SPS for Transformers at 400KV Bikaner (RVPNL)” operated and load feeders, e.g., 220KV Bikaner(RS)-Nokha Ckt & 220KV Bikaner(RS)-Sri Dungargarh Ckt tripped on SPS operation as per logic. v)Tripping of 220KV Bikaner(RS)-Nokha Ckt & 220KV Bikaner(RS)-Sri Dungargarh Ckt further caused overloading of 400/220 KV 315 MVA ICT 1 & 2 at Bikaner(RS) and both the ICTs tripped due to overloading. vi)As per PMU at Bikaner(IP), no fault was observed in the system, however fluctuation in voltage was present. vii)As per SCADA, change in NR total solar generation and Rajasthan solar generation of approx 405 MW and change in demand of approx 65 MW in Rajasthan contro | grid_india_gd/grid_events/2026-03-01
G00158 | 2026-03 | 45 | GD-1 | Odisha | OD | Eastern | 2026-03-12T06:36 | 2026-03-12T13:04 | 6.47 | 50 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Total generation loss of 50 MW reported at Rengali PH. | 1 GD-1 Odisha 12-03-2026 06:36 12-03-2026 13:04 06:28 50 0 0.15% 0.00% 33715 23007 At 06:36 Hrs on 12/03/2026, R-phase to Y-phase fault occurred in 220kV-TTPS-TSTPP line and fault was cleared from TSTPP end only further after 250 msec LBB operated at TTPS end. All emanating feeders from TTPS end tripped due to LBB operation (All feeders are connected through single bus). At the same time Rengali PH unit-1 also tripped in generator REF protection. 220kV TTPS S/s became dead. Total generation loss of 50 MW reported at Rengali PH. 220 kV TTPS-TSTPP 220 kV TTPS-NALCO 220 kV TTPS-Meramundali D/c 220 kV TTPS-Joda 220 kV TTPS-Telkoi 2*220/132 kV 160 MVA ATR at TTPS 220 kV Rengali PH-NALCO 220 kV Rengali PH-TSTPP 50 MW U#1 at Rengali PH | grid_india_gd/grid_events/2026-03-01
G00159 | 2026-03 | 15 | GD-1 | Punjab | PB | Northern | 2026-03-12T16:23 | 2026-03-12T18:19 | 1.93 | 0 | 122 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GD-1 Punjab 12-03-2026 16:23 12-03-2026 18:19 01:56 0 122 0.00% 0.22% 53333 56118 i)During antecedent condition, 400/66kV 250 MVA ICT 1 & 2 at HMEL (PS) were only in service and active power loading on ICTs were 64 MW and 62 MW respectively. ii)As reported, at 16:23 hrs, DT was sent from Behman J | 15 GD-1 Punjab 12-03-2026 16:23 12-03-2026 18:19 01:56 0 122 0.00% 0.22% 53333 56118 i)During antecedent condition, 400/66kV 250 MVA ICT 1 & 2 at HMEL (PS) were only in service and active power loading on ICTs were 64 MW and 62 MW respectively. ii)As reported, at 16:23 hrs, DT was sent from Behman Jassa Singh (PS) end due to PLCC maloperation during testing work. iii)Due to this, 400 KV Behman Jassa Singh (PS)-HMEL (PS) (PSTCL) Ckt-1 & 2 and 400 KV Behman Jassa Singh (PS)-Moga(PG) (PSTCL) Ckt-1 tripped respectively from HMEL(PS) and Moga(PG) end only. As per DR, DT received at HMEL(PS) and Moga(PG) end. iv)During the same time, 400/66 kV 250 MVA ICT 1 & 2 at HMEL (PS) also tripped (exact reason and nature of protection operation yet to be shared). This led to complete blackout at 400 kV HMEL(PS). v)As per PMU at Moga(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 122 MW was observed in Punjab control area. 1) 400 KV Behman Jassa Singh (PS)-HMEL (PS) (PSTCL) Ckt-1 2) 400 KV Behman Jassa Singh (PS)-HMEL (PS) (PSTCL) Ckt-2 3) 400 KV Behman Jassa Singh (PS)-Moga(PG) (PSTCL) Ckt-1 4) 400/66 kV 250 MVA ICT 1 at HMEL (PS) 5) 400/66 kV 250 MVA ICT 2 at HMEL (PS) | grid_india_gd/grid_events/2026-03-01
G00160 | 2026-03 | 31 | GI-1 | Maharashtra | MH | Western | 2026-03-13T15:14 | 2026-03-13T15:42 | 0.47 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GI-1 Maharashtra 13-03-2026 15:14 13-03-2026 15:42 00:28 - - - - 89345 73268 400/220 kV Kalwa (MSETCL)S/S:At 15:13 hrs / 13-03-2026, 220 kV Kalwa-GTPL-1 S/C snapped at the gantry top hardware at 220 kV Kalwa. 220 kV Kalwa-GTPL-1 S/C tripped on differential protection operation on R-E fault. 220 kV Kalwa-Temghar-1 S/C and 220 kV Kalwa-Salset-5 tripped on Zone-4 distance protection operation. 220/100 kV Kalwa-ICT-3&4 (200 MVA Each) tripped on B/U overcurrent operation. After 5 seconds, the R and Y-phase conductors of the 220kV Bus-Section (between the CB and Creek side Bus-section Isolator) resulting in busbar protection operation in 220 kV Kalwa (Creek Side) (Double main and transfer bus scheme) and all connected elements. Prior to the incident, 220 kV Navi Mumbai(PG)-Taloja-1 S/C was under planned outage for reconductoring work. 220 kV GTPL, 220 kV Panchanand and 220 kV Taloja were radially fed from 220 kV Kalwa station through 220 kV Kalwa-GTPL-1 S/C. Load loss of 547 MW occurred at Kalwa and associated downstream network. 1. 220 kV Kalwa-Bus-2 (Creek Side) 2. 220 kV Kalwa-GTPL-1 S/C 3. 220 kV Kalwa-Temghar-1 S/C 4. 220 kV Kalwa-Salset-5 S/C 5. 220 kV Kalwa-AKP-1 S/C 6. 220 kV GTPL-Panchanand-1 S/C 7. 220 kV Panchanand-Taloja-1 S/C 8. 220 kV Kalwa-PrintHouse-1 S/C 9. 220/100 kV Kalwa-ICT-1 200 MVA 10. 220/100 kV Kalwa-ICT-2 200 MVA 11. 220/100 kV Kalwa-ICT-3 200 MVA 12. 220/100 kV Kalwa-ICT-4 200 MVA Elements Tripped Details of Grid Events during the Month of March 2026 in | grid_india_gd/grid_events/2026-03-01
G00161 | 2026-03 | 46 | GD-1 | Odisha | OD | Eastern | 2026-03-14T04:23 | 2026-03-14T06:02 | 1.65 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 2 GD-1 Odisha 14-03-2026 04:23 14-03-2026 06:02 01:39 0 0 0.00% 0.00% 32134 23547 At 04:23 Hrs on 14/03/2026, B-phase to earth fault occurred in 220kV-TTPS-TSTPP line and fault was cleared from TSTPP end only further due to non opening of CB at TTPS end, LBB operated . All emanating feeders from TTPS end tripped due to LBB operation (All feeders are connected through single bus). 220kV TTPS S/s became dead. 220 kV TTPS-TSTPP 220 kV TTPS-NALCO 220 kV TTPS-Meramundali D/c 220 kV TTPS-Joda 220 kV TTPS-Telkoi 2*220/132 kV 160 MVA ATR at TTPS 220 kV Rengali PH-NALCO 220 kV Rengali PH-TSTPP Elements Tripped Details of Grid Events during the Month of March 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD I Manipur 02-03-2026 11:08 02-03-2026 11:59 00:51 0 0.4 0.00% 0.02% 1304 2081 Tipaimukh area of Manipur Power System was connected with rest of NER Grid through 132 kV Aizawl - Tipaimukh Line and 132 kV Jiribam - Tipaimukh Line. At 11:08 Hrs | grid_india_gd/grid_events/2026-03-01
G00162 | 2026-03 | 16 | GI-2 | Uttar Pradesh | UP | Northern | 2026-03-15T12:00 | 2026-03-19T01:55 | 85.92 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | No load loss or generation loss was observed in UP control area. | 16 GI-2 Uttar Pradesh 15-03-2026 12:00 19-03-2026 01:55 13:55 0 0 0.00% 0.00% 53800 45732 i)During antecedent condition, 800 KV HVDC Agra-BNC Pole-1 & 2 was carrying total 500 MW power from Agra to BNC (250 MW on each Pole). Pole-3 & Pole-4 at Agra & APD was out on Voltage Regulation. ii)As reported, at 12:00:49 hrs, DC Line Fault Level was detected in 800kV HVDC Agra-BNC Line-1. Subsequently, one restart aƩempt was taken by control system at full voltage as per implemented HVDC control logic. Line could not hold as fault did not clear during restart due to persistent fault & the control system blocked the converters at both ends. As per line fault locator, fault distance was 298.4 km from Agra(PG) at Tower no. 3631/A-8 (136/5) (under Lucknow TLM jurisdiction). iii)Further, at 12:00:55 hrs, DC Line Fault Level was detected in 800kV HVDC Agra-BNC Line-2 also. Subsequently, one restart aƩempt was taken by control system at full voltage as per implemented HVDC control logic. Line could not hold as fault did not clear during restart due to persistent fault & the control system blocked the converters at both ends. As per line fault locator, fault distance was 296.5 km from Agra(PG) at Tower no. 3636/A-8 (under Lucknow TLM jurisdiction). iv)As per PMU at Agra(PG), no fault was observed in the system; however fluctuation in voltage was present. v)As per SCADA, power order changed from 500 MW to 0 MW . No load loss or generation loss was observed in UP control area. 1)800 KV HVDC Agr | grid_india_gd/grid_events/2026-03-01
G00163 | 2026-03 | 40 | GI-1 | TAMILNADU |  |  | 2026-03-17T15:15 | 2026-03-17T16:10 | 0.92 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GI-1 TAMILNADU 17-03-2026 15:15 17-03-2026 16:10 00:55 0.0 0.0 0.0 % 0.0 % None None Tripping of 230kV Bus-2 of TTPS of TNPGCL As per the reports submitted, the triggering incident was B-G fault in 230kV KKNPP TTPS line. During the fault, LBB operated at TTPS end and all elements connected to 230 | 13 GI-1 TAMILNADU 17-03-2026 15:15 17-03-2026 16:10 00:55 0.0 0.0 0.0 % 0.0 % None None Tripping of 230kV Bus-2 of TTPS of TNPGCL As per the reports submitted, the triggering incident was B-G fault in 230kV KKNPP TTPS line. During the fault, LBB operated at TTPS end and all elements connected to 230kV Bus-2 tripped. 230kV KKNPP TTPS | grid_india_gd/grid_events/2026-03-01
G00164 | 2026-03 | 32 | GD-1 | Maharashtra | MH | Western | 2026-03-17T17:12 | 2026-03-17T19:14 | 2.03 | 2 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 452 MW occurred at 400kV Tuljapur due to loss of evacuation path. | 8 GD-1 Maharashtra 17-03-2026 17:12 17-03-2026 19:14 02:02 2 - 0.00% - 86002 71221 Complete outage of 400 kV Tuljapur(Renew Green PSS1 Wind)S/S: At 17:12 hrs/ 17-03-2026, 400KV Konhali PSS 4 – Tuljapur (Ghandora) PSS-1 line tripped due to earth fault protection operation at Konhali end only due of CT flashover occurred at 33KV side feeder the 400KV Tuljapur PSS-1. Line restored at 19:11 Hrs/17.03.2026. During charging of ICT-1 at 20:17 hrs, the transformer tripped on overcurrent protection. Generation loss of 452 MW occurred at 400kV Tuljapur due to loss of evacuation path. 1. 400/33 kV Tuljapur PSS-1 ICT 2. 400kV Tuljapur Bus 1 3. 400kV Tuljapur Bus 2 4. 400 kV Tuljapur PSS-1-Konhali PSS-4 | grid_india_gd/grid_events/2026-03-01
G00165 | 2026-03 | 41 | GI-2 | Karnataka | KA | Southern | 2026-03-18T07:51 | 2026-03-18T08:08 | 0.28 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GI-2 KARNATAKA 18-03-2026 07:51 18-03-2026 08:08 00:17 0 0 0.0 % 0.0 % 50945.01 60881.94 Tripping of 400kV Bus-1 of 400kV Kalaburagi SS As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1 | 14 GI-2 KARNATAKA 18-03-2026 07:51 18-03-2026 08:08 00:17 0 0 0.0 % 0.0 % 50945.01 60881.94 Tripping of 400kV Bus-1 of 400kV Kalaburagi SS As per the reports submitted, while opening the bus reactor 400kV Bus-1 of Kalaburagi got tripped tripping all elements connected to the 400kV Bus-1 | grid_india_gd/grid_events/2026-03-01
G00166 | 2026-03 | 17 | GI-2 | Haryana | HR | Northern | 2026-03-18T14:42 | 2026-03-18T15:53 | 1.18 | 0 | 84 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-2 Haryana 18-03-2026 14:42 18-03-2026 15:53 01:11 0 84 0.00% 0.16% 44878 51581 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 1500 MW power from Champa to Kurukshetra (375 MW on each Pole). ii)As reported, to address suspect signal (NTAMC) from IEDs installed o | 17 GI-2 Haryana 18-03-2026 14:42 18-03-2026 15:53 01:11 0 84 0.00% 0.16% 44878 51581 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 1500 MW power from Champa to Kurukshetra (375 MW on each Pole). ii)As reported, to address suspect signal (NTAMC) from IEDs installed on 500 MVAR TCR Network Ring, it was identified that fiber port-15 of EFS-2 is low and the fiber was manually shifted to another port. iii)However, this action caused all SAS ring devices to turn suspect simultaneously, resulting in multiple filter bank DBI (Data Bit Invalid) alarms. Consequently, a “minimum filter unavailable” alarm was triggered on both Bipoles. iv)Further, at 14:42:18.616 hrs and 14:45:54.692 hrs respectively, Bipole-1 & 2 Filter Control Blocking was initiated due to filter power limit. v)After restoring the fiber to its original port, device reporting gradually returned to normal. However, several BCUs remained unresponsive. vi)A physical inspection revealed that these BCUs were in a hung state, which had contributed to the DBI alarms. Normal operation was restored after restarting the affected BCUs. vii)Further investigation identified an IP address conflict: the IP of the TCR EFS-1 switch was found to be the same as that of CK-1 Gateway-2 (10.22.91.4). viii)As per PMU at Kurukshetra(PG), no fault was observed in the system, however reduction in 3-ph voltage at 14:42 hrs and rise in 3-ph voltage at 14:46 hrs occurred. ix)As per SCADA, Change in demand of approx | grid_india_gd/grid_events/2026-03-01
G00167 | 2026-03 | 42 | GI-1 | Kerala | KL | Southern | 2026-03-18T15:26 | 2026-03-18T16:26 | 1 | 102 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GI-1 KERALA 18-03-2026 15:26 18-03-2026 16:26 01:00 102 0 0.0 % 0.0 % 56030.59 65843.31 Tripping of 220kV Bus-2 at Idduku PH of KSEB As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-2 of Idukki PH . Immediately, 220kV Bus-2 BBP operated and all elements connected t | 15 GI-1 KERALA 18-03-2026 15:26 18-03-2026 16:26 01:00 102 0 0.0 % 0.0 % 56030.59 65843.31 Tripping of 220kV Bus-2 at Idduku PH of KSEB As per the reports submitted, the triggering incident was B-G fault in 220kV Bus-2 of Idukki PH . Immediately, 220kV Bus-2 BBP operated and all elements connected to the Bus-2 tripped. 220KV-IDDUKI-KALAMASSERY-2, 220KV-IDDUKI- KOTHAMANGALAM-1, 220KV-LOWER PERIYAR-IDDUKI-2 | grid_india_gd/grid_events/2026-03-01
G00168 | 2026-03 | 18 | GI-2 | Haryana | HR | Northern | 2026-03-18T18:39 | 2026-03-18T20:06 | 1.45 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 800 KV HVDC Kurukshetra(PG) Pole-1 2) 800 KV HVDC Kurukshetra(PG) Pole-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of March 2026 in Northern Region Elements Tripped SlNo. | 18 GI-2 Haryana 18-03-2026 18:39 18-03-2026 20:06 01:27 0 0 0.00% 0.00% 48358 53986 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 700 MW power from Champa to Kurukshetra (175 MW on each Pole). In Bipole‑1, filters sub banks HACQ21 and HACQ31 (Type‑A), HACQ12 (Type‑B), and HACQ15 (Type‑D) were in service. ii)As reported, at 18:38:25.347 hrs, the status of the Type-A filter HACQ31 became suspect, prompting the HVDC control system to generate a DBI (Data Bit Invalid) alarm. Despite this, Bipole-1 continued operating with a filter configuration of 1A + 1B + 1D in service. iii)As per earlier operating practice, the loss of any A/B/C-type filter was typically mitigated by switching in a D-type filter to avoid Bipole tripping. Following this approach, the operator brought one additional D- type filter into service. However, this action triggered the “Filter Control TOVC Inhibit Filter Switch-In” alarm as the bus voltage was around 422kV. This inhibits the Filter switching in as the Bus voltage reaches beyond 425kV. iv)Subsequently, the Reactive Power Controller recalculated the minimum filter requirement as 2A + 1B. Since the available configuration (1A + 1B) did not meet this requirement, Bipole-1 was blocked on the Minimum Filter Requirement criterion. v)The primary cause of Bipole tripping is the lack of suﬃcient redundancy in Type-A and Type-B filters at both terminals of the Champa-Kurukshetra link. For bipolar opera tion, even at minimum load, | grid_india_gd/grid_events/2026-03-01
G00169 | 2026-03 | 19 | GD-1 | Haryana | HR | Northern | 2026-03-18T22:29 | 2026-03-19T00:50 | 2.35 | 0 | 37 | FALSE | FALSE | FALSE | FALSE | FALSE | 19 GD-1 Haryana 18-03-2026 22:29 19-03-2026 00:50 02:21 0 37 0.00% 0.08% 38836 46570 i)220/132kV Rewari(HV) has double main bus scheme at both 132kV and 220kV level. ii)As reported, at 22:29 hrs, during trial of 33kV feeder to Jonawas from Rewari, heavy flashover occurred which led to R-N phase to e | 19 GD-1 Haryana 18-03-2026 22:29 19-03-2026 00:50 02:21 0 37 0.00% 0.08% 38836 46570 i)220/132kV Rewari(HV) has double main bus scheme at both 132kV and 220kV level. ii)As reported, at 22:29 hrs, during trial of 33kV feeder to Jonawas from Rewari, heavy flashover occurred which led to R-N phase to earth fault. iii)220 KV Bhiwadi(PG)-Rewari(HV) (HVPNL) CKT-1 & 2 sensed this fault and both lines tripped in zone-2 protection operation from Bhiwadi(PG) end (Why protection not operated at Rewari end?). As per DR, fault currents were 5.62 kA and 5.45 kA respectively for 220 KV Bhiwadi(PG)-Rewari(HV) (HVPNL) CKT-1 & 2 from Bhiwadi(PG) end. iv)During the same time, 220 KV Lullaahir(HV)- Rewari(HV) (HVPNL) CKT-1 also tripped (exact reason of tripping and nature of protection operation yet to be shared). v)Due to tripping of both 220 KV Bhiwadi(PG)-Rewari(HV) (HVPNL) CKT-1 & 2 and 220 KV Lullaahir(HV)- Rewari(HV) (HVPNL) CKT-1, complete blackout occurred at 220/132kV Rewari(HV) S/s. vi)As per SCADA SOE, 400kV Bhiwadi-Hissar (PG) Ckt-1 also tripped at the same time (exact reason of tripping and nature of protection operation yet to be shared). vii)As per PMU at Bhiwadi(PG), R-N phase to earth fault was observed with delayed fault clearing time of 400 ms. viii)As per SCADA, change in demand of approx 37 MW was observed in Haryana control area. 1) 220 KV Bhiwadi(PG)-Rewari(HV) (HVPNL) CKT-1 2) 220 KV Bhiwadi(PG)-Rewari(HV) (HVPNL) CKT-2 3) 220 KV Lullaahir(HV)- Rewari(HV) (HVPNL) CKT-1 | grid_india_gd/grid_events/2026-03-01
G00170 | 2026-03 | 34 | GD-1 | Gujarat | GJ | Western | 2026-03-19T01:00 | 2026-03-19T02:36 | 1.6 | 324 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 205 MW occurred at Khavda PSS 8 due to loss of evacuation path. | 10 GD-1 Gujarat 19-03-2026 01:00 19-03-2026 02:36 01:36 324 - 0.45% - 72084 64009 Complete outage of Inclement weather condition in Gujarat • At 01:00 Hrs/19032026, 400 kV Khavda PS3- Khavda PSS 8 tripped on Y-B phase fault. Generation loss of 205 MW occurred at Khavda PSS 8 due to loss of evacuation path. • At 01:22 Hrs/19032026, 220 kV Bhuj- Baranda tripped on B-E fault. Generation loss of 108 MW occurred at 220 kV Baranda due to loss of evacuation path. • At 01:25 Hrs/19032026, 220 kV Bhuj- Ratadiya 2 tripped on R-E fault. 220 kV Ratadiya station remain intact through 220 kV Bhuj- Ratadiya 1. • At 01:32 Hrs/19032026, 220 kV Bhuj- Vadva auto reclosed successfully on R-E fault. • At 01:34 Hrs/19032026, 220 kV Bhuj- Zhura tripped on R-E fault. During the same time, 220 kV Bhuj- Gadhsisa tripped at Gadhsisa end only. Generation loss of 0 MW (solar plant) & 33 MW occurred at 220 kV Zhura & 220 kV Gadhsisa respectively due to loss of evacuation path. • At 01:44 Hrs/19032026, 765 kV Bhuj II- Bhuj ckt 1 & 765 kV Khavda PS1- Bhuj 1 auto reclosed successfully on B-E fault. • 400 kV APL- Mansar, 400 kV APL- Charanka & 400 kV APL- Sami II tripped on B-E fault respectively at 02:06 Hrs, 02:54 Hrs & 03:05 Hrs respectively. 1. 400 kV Khavda PS3- KPSS 8 2. 220 kV Bhuj- Baranda 3. 220 kV Bhuj- Ratadiya 2 4. 220 kV Bhuj- Vadva 5. 220 kV Bhuj- Zhura 6. 220 kV Bhuj- Gadhsisa 7. 765 kV Bhuj II- Bhuj ckt 1 8. 765 kV Khavda PS1- Bhuj 1 9. 400 kV APL- Mansar 10. 400 kV APL- Sami II 11. 400 kV APL | grid_india_gd/grid_events/2026-03-01
G00171 | 2026-03 | 33 | GD-1 | Gujarat | GJ | Western | 2026-03-19T14:25 | 2026-03-19T17:06 | 2.68 | 46 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 46 MW occurred at Baranda (Avikiran) Wind power plant due to loss of evacuation path. | 9 GD-1 Gujarat 19-03-2026 14:25 19-03-2026 17:06 02:41 46 - 0.06% - 73839 67305 Complete outage of 220 kV Baranda S/S (Avikiran): At 14:25 hrs / 19-03-2026, 220 kV Bhuj-Baranda-1 S/C tripped on persistent B-E fault (auto recloser unsuccessful). No abnormalities were found during patrolling by Avikiran. Generation loss of 46 MW occurred at Baranda (Avikiran) Wind power plant due to loss of evacuation path. 1. 220kV Bhuj-Baranda Line 2. 220/33kV 150 MVA Baranda ICT-1 3. 220/33kV 150 MVA Baranda ICT-2 4. 220kV Bus-1 5. 220kV Bus-2 | grid_india_gd/grid_events/2026-03-01
G00172 | 2026-03 | 20 | GI-2 | Uttar Pradesh | UP | Northern | 2026-03-20T07:16 | 2026-03-20T10:31 | 3.25 | 590 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 590 MW was observed at Bara TPS (UP). | 20 GI-2 Uttar Pradesh 20-03-2026 07:16 20-03-2026 10:31 03:15 590 0 1.34% 0.00% 44132 44800 i)765/400kV Bara TPS(UP) has oner and half breaker scheme at both 765kV and 400kV level. ii)During antecedent condition, 660 MW Unit-1, 2 & 3 at Bara TPS(UP) were in running condition and generating approx 590 MW each (as per SCADA). iii)As reported, at 07:16 hrs, 765kV Bara-Mainpuri(UP) Ckt-2 auto-reclosed successfully on transient Y-N phase to earth fault with fault distance 53.2 m from Bara(UP) end. As per DR, fault current was 16.8 kA from Bara(UP) end; fault sensed in zone-1 at Bara(UP) end. iv)During A/R dead time, 765/400kV 1500 MVA ICT-2 tripped on differential and REF protection operation (as per DR) sensing this fault (exact reason of tripping need to be shared). v)During the same time, 660 MW Unit-1 at Bara TPS(UP) also tripped on LSR (Load Surge Relay) operation (exact reason of tripping need to be shared). vi)As per PMU at Mainpuri(PG), Y-N phase to earth fault was observed with fault clearing time of 80 ms. vii)As per SCADA, generation loss of approx 590 MW was observed at Bara TPS (UP). 1) 660 MW Unit-1 at Bara TPS(UP) 2) 765/400kV 1500 MVA ICT-2 at Bara(UP) | grid_india_gd/grid_events/2026-03-01
G00173 | 2026-03 | 43 | GI-2 | Karnataka | KA | Southern | 2026-03-20T08:03 | 2026-03-20T09:38 | 1.58 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GI-2 KARNATAKA 20-03-2026 08:03 20-03-2026 09:38 01:35 0 0 0.0 % 0.0 % 45939.24 58069.32 Tripping of 400kV Bus-2 of 400kV Doni S of KPTCL As per the reports submitted, the triggering incident was B-G fault in 400kV Bus-2 due to B-phase limb flashover during Bus reactor CB operation. Immediately, | 16 GI-2 KARNATAKA 20-03-2026 08:03 20-03-2026 09:38 01:35 0 0 0.0 % 0.0 % 45939.24 58069.32 Tripping of 400kV Bus-2 of 400kV Doni S of KPTCL As per the reports submitted, the triggering incident was B-G fault in 400kV Bus-2 due to B-phase limb flashover during Bus reactor CB operation. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped resulting is loss of power supply to 400kV Dhoni Bus-2. It is reported that the Tie breaker of 400kV/220kV Dhoni ICT-1 was hand tripped by the shift engineer during fault. This led to the loss of power supply to tripping of 400kV/220kV Dhoni ICT-1. DONI - 400KV - Bus 2, 400KV/220KV DONI-ICT-1 | grid_india_gd/grid_events/2026-03-01
G00174 | 2026-03 | 35 | GD-1 | Gujarat | GJ | Western | 2026-03-21T04:43 | 2026-03-24T08:29 | 75.77 | 10 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 10 MW occurred at 220/33kV AEPL Nana Valka substation due to loss of the evacuation path. | 11 GD-1 Gujarat 21-03-2026 04:43 24-03-2026 08:29 75:46 10 - 0.02% - 64064 57892 Complete outage of220/33kV Nanavalka (Wind) Giwel-III: At 04:43 hr / 21.03.2026, the 220KV-Nanavalka-Alfanar-Bhuj-1 line tripped due to an B-Y fault. Generation loss of 10 MW occurred at 220/33kV AEPL Nana Valka substation due to loss of the evacuation path. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C2. 220/33kV Alfanar ICT-13. 220/33kV Alfanar ICT-2 | grid_india_gd/grid_events/2026-03-01
G00175 | 2026-03 | 21 | GD-1 | Uttar Pradesh, Uttarakhand |  |  | 2026-03-23T10:10 | 2026-03-23T12:09 | 1.98 | 80 | 85 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 80 MW occurred at Alakhnanda HEP . | 21 GD-1 Uttar Pradesh, Uttarakhand 23-03-2026 10:10 23-03-2026 12:09 01:59 80 85 0.15% 0.17% 53024 48726 i)400kV Alaknanda(UP) has one and half breaker scheme at 400kV level. ii)During antecedent condition, only one bus was in service at 400kV Alakhnanda(UP) and all the elements were connected to the same bus. Only 82.5 MW Alaknanda GVK (UPC) Unit-2 was in running condition through tie CB and was generating approx 80 MW (as per SCADA). There was no generation at 220KV Singoli Bhatwari HEP and 220 KV Singoli Bhatwari (Singoli(LTUHP))- Srinagar (UK) (PTCUL) Ckt-1 and Ckt-2 were in unloaded condition. iii)As reported, at 10:10 hrs, B-Ph CT flashover occurred at 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK) Ckt-2 which led to busbar protection operation at 400 KV Alakhnanda(UP). iv)As per DR at Srinagar(UK) end of of 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK) Ckt-2, B-N phase to earth fault was observed with fault current of ~2.379kA from Srinagar end and line CB ta Srinagar end tripped on sensing the fault in zone-2 with carrier received from Alaknanda end. v)Due to bus bar operation all transmission elements connected to 400 KV Alaknanda(UP) along with 82.5 MW Alaknanda GVK (UPC) Unit-2 tripped and complete blackout occurred at 400kV Alaknanda(UP) S/s. vi)As per PMU at Koteshwar(PG), B-N Phase to earth fault was observed with fault clearing time of 80 ms. vii)As per SCADA, change in demand of approx 85 MW was observed in UƩarakhand control area. Generation loss of approx 80 MW o | grid_india_gd/grid_events/2026-03-01
G00176 | 2026-03 | 36 | GD-1 | Gujarat | GJ | Western | 2026-03-23T20:01 | 2026-03-23T20:39 | 0.63 | 210 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 168 MW and 47 MW occurred at Baranda (Avikiran) and at Gadhsisa (Renew Power) Wind power plants respectively due to loss of evacuation path. | 12 GD-1 Gujarat 23-03-2026 20:01 23-03-2026 20:39 00:38 210 - 0.28% - 74811 67491 Complete outage of 220 kV Baranda (Avikiran) & 220kV Gadhsisa (Renew): 1. At 20:01 hrs / 23-03-2026, 220 kV Bhuj-Baranda-1 S/C tripped on Y-E fault, simultaneously 220 kV Bhuj-Gadhsisa-1 S/C tripped from Gadhsisa end only. Burnt conductor was found near gantry number 11 at Powergrid end due to suspected conductor theft attempt. Generation loss of 168 MW and 47 MW occurred at Baranda (Avikiran) and at Gadhsisa (Renew Power) Wind power plants respectively due to loss of evacuation path. 1. 220kV Bhuj Gadhsisa S/C 2. 220kV Bhuj Baranda S/C | grid_india_gd/grid_events/2026-03-01
G00177 | 2026-03 | 22 | GD-1 | Rajasthan | RJ | Northern | 2026-03-24T15:14 | 2026-03-24T17:18 | 2.07 | 630 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per PMU & SCADA, Total generation loss of approx 630 MW was observed at RSDCL 1 (~228 MW), RSDCL 2 (~205 MW) & RSDCL 3 (~197 MW). | 22 GD-1 Rajasthan 24-03-2026 15:14 24-03-2026 17:18 02:04 630 0 1.25% 0.00% 50312 43150 i)220kV RSDCL-1, 2 &3 (IP) were connected at Bhadla2(PG) at 220kV level and their generation evacuate through 220 KV Bhadla_2 (PG)-RSDCL(PSS1)_SL_BHD2_PG (RSDCL) Ckt, 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt and 220 KV Bhadla_2 (PG)-RSDCL(PSS3)_SL_BHD2_PG (RSDCL) Ckt respectively. ii)During antecedent condition, 220kV RSDCL-1, 2 &3 (IP) were generating approx 228 MW (as per PMU, SCADA data freezed), 205 MW ( as per SCADA, PMU data not available) and 197 MW (as per PMU, SCADA data freezed) resepectively with a cumulative total generation of approx 630 MW. iii)As reported at 15:14 hrs, 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt tripped on Y-N phase to earth fault with fault distance of 11.91 km From RSDCL-2 end due to Y-phase jumper broken; fault sensed in zone-1 at RSDCL-2 end. iv)During the same time, 220 KV Bhadla_2 (PG)-RSDCL(PSS1)_SL_BHD2_PG (RSDCL) Ckt and 220 KV Bhadla_2 (PG)-RSDCL(PSS3)_SL_BHD2_PG (RSDCL) Ckt also tripped from RSDCL end (exact reason of tripping and nature of protection operated yet to be shared). v)Due to tripping of these evacuating lines, complete blackout occurred at 220kV RSDCL-1, 2 &3 (IP). vi)As per PMU at Bhadla2(PG), Y-N phase to earth fault was observed with fault clearing time of 80 ms. vii)As per PMU & SCADA, Total generation loss of approx 630 MW was observed at RSDCL 1 (~228 MW), RSDCL 2 (~205 MW) & RSDCL 3 (~197 MW). 1) 220 | grid_india_gd/grid_events/2026-03-01
G00178 | 2026-03 | 37 | GD-1 | Madhya Pradesh | MP | Western | 2026-03-24T16:51 | 2026-03-24T21:07 | 4.27 | 61 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 61 MW at Taletutayi Solar RE Plant occurred due to loss of evacuation path. | 13 GD-1 Madhya pradesh 24-03-2026 16:51 24-03-2026 21:07 05:02 61 - 0.07% - 84797 72978 Complete outage of 220 kV ShajapurU-8 S/S Taletutayi: At 16:51 hrs/ 24-03-26, 220kV Taletutayi Pachora line tripped due to differential protection operated. Generation loss of 61 MW at Taletutayi Solar RE Plant occurred due to loss of evacuation path. 1. 220kV Pachora Taletutayi | grid_india_gd/grid_events/2026-03-01
G00179 | 2026-03 | 44 | GI-1 | TAMILNADU |  |  | 2026-03-26T17:57 | 2026-03-26T21:47 | 3.83 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 17 GI-1 TAMILNADU 26-03-2026 17:57 26-03-2026 21:47 03:50 0 0 0.0 % 0.0 % 50362.52 58654.11 Tripping of 230kV Bus-1 of Karaikudi SS of TANTRANSCO As per the reports submitted, the triggering incident was B-G fault in 230kV Karaikudi Bus-1 and BBP operated tripping all elements connected to the 230kV Karaikudi Bus-1. 230KV-KARAIKUDI(TN)-KAVANUR-1, 230KV-KARAIKUDI(TN)- KAVANUR-3, 230KV-KARAIKUDI(TN)-KAVANUR-4, 230KV- KARAIKUDI-KARAIKUDI(TN)-1, 230KV-KARAIKUDI(TN)- KARAMBAYAM-1 Details of Grid Events during the Month of March 2026 in Southern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-03-01
G00180 | 2026-03 | 23 | GI-2 | Rajasthan | RJ | Northern | 2026-03-27T15:32 | 2026-03-27T18:20 | 2.8 | 1166 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)At the same time, change in NR total solar generation of approx 1166 MW and ~255 MW in Rajasthan Solar generation (as per SCADA) is observed. | 23 GI-2 Rajasthan 27-03-2026 15:32 27-03-2026 18:20 02:48 1166 0 2.09% 0.00% 55664 44698 i)400/220kV Bikaner(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)During antecedent condition, 400 KV Bikaner(RS)-Deedwana(MTS) (RS) Ckt-1 and 400 KV Suratgarh(RVUN)-Bikaner(RS) (RS) Ckt-1 were carrying 482 MW & 92 MW respectively. iii)As reported, at 14:28 hrs, fire incident occurred in 125 MVAr Bus reactor-2 due to internal fault and bus reactor tripped on Differential protection. It took around 4-5 hours to get fire extinguished. iv)Due to fire incident in Bus Reactor, at 15:32 hrs, 400kV Suratgarh(RVUN)- Bikaner(RS) (RS) CKT-1 and 400 kV Bikaner(RS)-Deedwana(MTS) (RS) CKT-1 tripped on Y-B fault. Bikaner(RS) end distance protection of 400 kV Bikaner(RS)-Deedwana(MTS) (RS) CKT-1 sensed the fault in Z-1 (~242 meter) and fault currents were Iy=19.1 kA, Ib=18.44 kA from Bikaner end and distance-123.6km (Z-2), Iy=1.5kA, Ib=2.5kA from Deedwana(RS) end. Reason of tripping of 400kV Suratgarh(RVUN)- Bikaner(RS) (RS) CKT-1 not received yet. v)As per PMU at Bhadla(PG), Y-B phase to phase fault was observed with fault clearing time of 80 msec. vi)At the same time, change in NR total solar generation of approx 1166 MW and ~255 MW in Rajasthan Solar generation (as per SCADA) is observed. Out of 1166 MW, approx 520 MW total NR solar generation recovered within 01 minute of the occurrence of event. No change in demand in Rajasthan control | grid_india_gd/grid_events/2026-03-01
G00181 | 2026-03 | 24 | GI-2 | Uttar Pradesh | UP | Northern | 2026-03-28T00:52 | 2026-03-28T02:58 | 2.1 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 500 KV HVDC Balia-Bhiwadi (PG) Ckt-1 2) 500 KV HVDC Balia-Bhiwadi (PG) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 24 GI-2 Uttar Pradesh 28-03-2026 00:52 28-03-2026 02:58 02:06 0 0 0.00% 0.00% 37525 46815 i)During antecedent condition, 500kV HVDC Balia-Bhiwadi Pole-1 & 2 was carrying total 300 MW power from Balia to Bhiwadi (150 MW on each Pole). ii)As reported, at 00:52:19 hrs, 500 KV HVDC Balia-Bhiwadi (PG) Ckt-1 &2 tripped from Balia end on “RPC No AC Filter” due to DC and AC mixing. iii)As per DC station control configuration, if the number of connected sub banks is below the minimum configuration (1 for monopole, 2 for Bipole) the message "RPC NO AC FILTER" will be generated, and a delay of two seconds is provided to give time for the automatic AC filter control switching on a substitute sub bank. After that two second delay, tripping of the converters is initiated. iv)As reported by power grid, filter 10CF11 and 10CF22 were in service and next filter to be with switched was 10CF21. At 00:52:14:786 hrs, Transformer L1 AC supply fault had appeared, and a sequence of event of changing filter breaker and disconnector status was generated. At 00:52:15:371, filter 10CF11, 10CF13, 10CF21, 10CF22, automatic status was dropped (it means filters won’t be able to switch automatically). At 00:52:15:648, AC filter fence key area tripped alarm was generated which suggests mixing of AC & DC source. At 00:52:17:37, “RPC no filter” Emergency alarm was generated which did not get reset and after 2 sec, Poles were blocked by DC station control. v)As per PMU at Balia (PG), no fault was observed in the | grid_india_gd/grid_events/2026-03-01
G00182 | 2026-03 | 39 | GD-1 | Madhya Pradesh | MP | Western | 2026-03-30T12:03 | 2026-03-30T12:52 | 0.82 | 116 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss of 116.31 MW occurred at 220 kV ShajapurU-7 S/S Dehripal power plants respectively due to loss of evacuation path. | 15 GD-1 Madhya pradesh 30-03-2026 12:03 30-03-2026 12:52 00:49 116 - 0.64% - 18059 10165 Complete outage of 220 kV Shajapur U-7 S/S Dehripal: At 12:03 Hrs / 30.03.2026, 220KV-SHAJAPUR Unit-6(Burlay)-SHAJAPUR Unit-7(Dehripal)-12 line tripped on Y-B ph fault due to operation of differential protection. Generation loss of 116.31 MW occurred at 220 kV ShajapurU-7 S/S Dehripal power plants respectively due to loss of evacuation path. 1 220kV Pachora Dehripal-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 KARNATAKA 03-03-2026 11:00 03-03-2026 11:40 00:40 556 665 0.01 % 0.01 % 55465.17 68490.91 Complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Kalburgi of KPTCL In the antecedent conditions, multiple bus splits were carried out in the vicinity of 400/220 kV Kalburgi substation to facilitate evacuation of RE power. The triggering incident was the tripping of 400/220kV ICT-1 and 2 at Kalburgi substation. Since multiple substations were radially connected through Kalburgi, the tripping of the ICTs led to the complete outage of 220 kV Aheri, Nimbarga, Vaishali, Shahbad, Kapnoor, Humnabad, Gulbarga, and Santhapur and tripping of 220 kV Bijapur Bus-2, Shahpur Bus-2, Sedam Bus-2, and Bus-1 & Bus-2 at Ferozabad(Kalb | grid_india_gd/grid_events/2026-03-01
G00183 | 2026-03 | 38 | GI-2 | Maharashtra | MH | Western | 2026-03-30T22:24 | 2026-03-31T02:40 | 4.27 | 285 |  | FALSE | FALSE | FALSE | FALSE | FALSE | During the charging attempt, 400 kV Jaigad Bus-2 tripped along with the 400 kV Jaigad–New Koyna-2 line and Jaigad Unit-3 (300 MW) due to LBB operation because of fault in the line, resulting in a generation loss of 285 MW. | 14 GI-2 Maharashtra 30-03-2026 22:24 31-03-2026 02:40 04:16 285 - 0.38% - 75277 63420 Partial outage of 400 kV Jaigad: At 22:07 Hrs / 30.03.2026, the 400 kV Jaigad–Karad-2 line tripped. After replacing punctured insulators at tower locations 51 and 52, a charging attempt was taken at 22:24 Hrs / 31.03.2026. During the charging attempt, 400 kV Jaigad Bus-2 tripped along with the 400 kV Jaigad–New Koyna-2 line and Jaigad Unit-3 (300 MW) due to LBB operation because of fault in the line, resulting in a generation loss of 285 MW. 1. 400kV Jaigad-Karad-2 2. 400kV Jaigad Bus-2 3. 400kV Jaigad-New Koyna-2 4. Jaigad Unit-3 (300 MW) | grid_india_gd/grid_events/2026-03-01
G00184 | 2026-04 | 27 | GI-2 | Maharashtra | MH | Western | 2026-04-01T22:38 | 2026-04-02T02:05 | 3.45 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | No load loss or generation loss Occurred during this event. | 1 GI-2 Maharashtra 01-04-2026 22:38 02-04-2026 02:05 03:27 - - - - 64725 76790 Partial outage of 400kV Khaparkheda (MSETCL): At 22:38 hrs / 01-04-2026, 400 kV Khaparkheda-Bus-2 tripped on Busbar protection operation (one and half breaker scheme), resulting in tripping of all connected main bays. Simaltaneously, Tie bays of 400 kV Khaparkheda-Koradi-1 and 400 kV Khaparkheda-Koradi-2 tripped, resulting in tripping of respective lines. As per MSETCL report, 400 kV Khaparkheda-Koradi-2 Tie bay tripped at Khaparkheda end on TEED protection operation and 400 kV Khaparkheda-Koradi-2 tripped on Neutral Displacement Relay Operated. As observed in disturbance recorder, both 400 kV Khaparkheda-Koradi-1&2 D/C tripped due on busbar protection operation and Direct Trip was sent to remote end. No load loss or generation loss Occurred during this event. 1. 400 kV Khaparkheda-Bus-2 2. 400 kV Khaparkheda-Koradi-1 3. 400 kV Khaparkheda-Koradi-2 4. 400/220 kV Khaparkheda-ICT-1 | grid_india_gd/grid_events/2026-04-01
G00185 | 2026-04 | 28 | GD-1 | Gujarat | GJ | Western | 2026-04-02T11:57 | 2026-04-02T13:28 | 1.52 | 226 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss of 226 MW occurred at 220kV Gadhsisa RE station due to loss of evacuation path. | 2 GD-1 Gujarat 02-04-2026 11:57 02-04-2026 13:28 01:31 226 - 0.30% - 76007 64969 Complete outage of 220kV Gadhsisa(Renew Power):At 11:57 hrs/ 02-04-2026, 220kV Bhuj–Gadhsisa line tripped due to Y phase to ground fault. Generation loss of 226 MW occurred at 220kV Gadhsisa RE station due to loss of evacuation path. 1. 220kV Bhuj-Gadhsisa S/C | grid_india_gd/grid_events/2026-04-01
G00186 | 2026-04 | 42 | GD-1 | West Bengal | WB | Eastern | 2026-04-02T14:28 | 2026-04-02T15:28 | 1 | 413 | 782 | FALSE | FALSE | FALSE | FALSE | FALSE | 220kV Bidhananagr, Ab Zone, and DPL became dead and generation loss of 413 MW at DPL and load loss of 782 MW reported at Bidhannagar, AB Zone. | 1 GD-1 West Bengal 02-04-2026 14:28 02-04-2026 15:28 01:00 413 782 1.77% 3.00% 23357 26100 Prior to the disturbance, 315 MVA ICT-3 at Bidhannagar S/s was under planned shutdown. At 14:20 Hrs of 02/04/2026, 315 MVA ICT-1 tripped due to PRD operation, which led to over loading of 315 MVA ICT-2(Loading increased up to 336 MW). To reduce the loading on ICT-2, 220kV Mangalpur and Shyam SEL feeder were manually tripped at 14:24 Hrs. Consequently, the loading on ICT-2 reduced to a safe limit of around 275 MW. Subsequently, at 14:28 Hrs, 315 MVA ICT-2 was inadvertently hand tripped by site personal, which led to isolation of 220kV from 400kV system Simultaneously, 220kV Bidhannagar-Bakreswar D/C loading increased up to its thermal rating, causing both lines tripped on O/C protection. As a result, 220/132kV Bidhannagar islanded with AB Zone and DPL generation and got collapsed due to load generation unbalance. 220kV Bidhananagr, Ab Zone, and DPL became dead and generation loss of 413 MW at DPL and load loss of 782 MW reported at Bidhannagar, AB Zone. 400/220KV ICT-1 at Bidhannagar 400/220KV ICT-2 at Bidhannagar DPL Unit-7 DPL Unit-8 | grid_india_gd/grid_events/2026-04-01
G00187 | 2026-04 | 3 | GI-2 | Haryana | HR | Northern | 2026-04-04T01:31 | 2026-04-04T04:03 | 2.53 | 0 | 423 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GI-2 Haryana 04-04-2026 01:31 04-04-2026 04:03 02:32 0 423 0.00% 0.93% 39918 45458 i)400/220kV Daulatabad(HV) has double main bus scheme at 220kV level and one and half breaker scheme at 400kV level. ii)During antecedent condition, 400/220 kV 315 MVA ICTs 1, 2, 3 and 4 at Daulatabad (HV) were carr | 3 GI-2 Haryana 04-04-2026 01:31 04-04-2026 04:03 02:32 0 423 0.00% 0.93% 39918 45458 i)400/220kV Daulatabad(HV) has double main bus scheme at 220kV level and one and half breaker scheme at 400kV level. ii)During antecedent condition, 400/220 kV 315 MVA ICTs 1, 2, 3 and 4 at Daulatabad (HV) were carrying 100 MW , 86 MW , 101 MW and 86 MW respectively from 400kV side to 220Kv side (as per SCADA). iii)As reported, at 01:31 hrs, 220kV side B-phase CT of 400/220 KV 315 MVA ICT 1 at Daulatabad(HV) got damaged. iv)During the same time, all four 400/220 KV 315 MVA ICTs at Daulatabad(HV) tripped on over current earth fault relay operation (exact reason of tripping yet to be shared). v)As per PMU at Gurgaon(PG), B-N fault followed by B-N fault converted to Y-B-N fault again followed by R-Y fault converted to R-Y-B fault were observed with fault clearing time of 80 ms, 640 ms (delayed) and 800 ms (delayed) respectively. vi)As per SCADA, Change in Demand of approx 423 MW at Haryana Control area. 1) 400/220 kV 315 MVA ICT 1 at Daulatabad (HV) 2) 400/220 kV 315 MVA ICT 2 at Daulatabad (HV) 3) 400/220 kV 315 MVA ICT 3 at Daulatabad (HV) 4) 400/220 kV 315 MVA ICT 4 at Daulatabad (HV) | grid_india_gd/grid_events/2026-04-01
G00188 | 2026-04 | 2 | GD-1 | Himachal Pradesh | HP | Northern | 2026-04-04T13:44 | 2026-04-04T22:48 | 9.07 | 22 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 22 MW was observed at Himachal Pradesh control area. | 2 GD-1 Himachal Pradesh 04-04-2026 13:44 04-04-2026 22:48 09:04 22 0 0.04% 0.00% 53938 42387 i)220/132/33kV Charor(HP) has double main bus scheme at 220kV level, 132kV level and 33kV level. 400/220kV Banala(HP) has Double main bus scheme at both 400kV level and 220kV level. ii)During antecedent condition, 220 KV Charor(HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-1 & 2 were carrying 10 MW each from Charor to Banala. iii)As reported, at 13:44 hrs, 220 KV Charor(HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-1 tripped on R-Y-N double phase to earth fault with fault distance of 1.6 km from Charor end. iv)During the same time, 220 KV Charor(HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-2 also tripped on R-Y-N double phase to earth fault with fault distance of 4.2 km from Charor end. v)As per SCADA SOE, 220/33 kV ICT-1 at Charor (HP) also tripped during the same time (exact reason and nature of protection operation yet to be shared). vi)As per PMU at Nallagarh(PG), R-Y-N phase to phase to earth fault was observed with fault clearing time of 80 msec. vii)As per SCADA, generation loss of approx 22 MW was observed at Himachal Pradesh control area. 1) 220 KV Charor (HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-1 2) 220 KV Charor (HP)-Parbati Pooling Banala(PG) (HPPTCL) Ckt-2 | grid_india_gd/grid_events/2026-04-01
G00189 | 2026-04 | 1 | GI-2 | Rajasthan | RJ | Northern | 2026-04-04T16:34 | 2026-04-04T18:09 | 1.58 | 540 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 540 MW was observed at Chhabra SCTPS. | 1 GI-2 Rajasthan 04-04-2026 16:34 04-04-2026 18:09 01:35 540 0 1.04% 0.00% 52132 47355 i)765/400kV Anta(RS) has one and half breaker scheme at both 765kV level and 400kV level. ii)During antecedent condition, 765 kV Anta-Phagi (RS) Ckt-1 was carrying 1039 MW from Anta to Phagi and total generation of Chhabra SCTPS was 1030 MW. iii)As reported, at 16:34 hrs, 765 kV Anta-Phagi (RS) Ckt-1 tripped only from Anta end on B-N phase to earth fault with fault current of 9.846 kA from Anta and 4.316 kA from Phagi (as per DR) due to bad weather. As per DR, fault sensed in zone-2 and carrier received at Phagi end; A/R successfully operated at Phagi end, however no A/R operation observed at Anta end and line tripped from Anta end on zone-1 distance protection operation. iv)During the same time, 765/400 KV 1500 MVA ICT 1, 2 and 3 at Anta(RS) also tripped on differential protection operation on consecutive B-N phase to earth faults followed by Y-N phase to earth fault respectively (exact reason of fault yet to be shared). v)Due to tripping of all 3 ICTs at 765/400 kV Anta (RS), “SPS related to Safe evacuation of generation of Chhabra/ Chhabra Super Critical/ Kawai/ Kalisindh Complex” operated (case-1 of Chhabra, Kawai and Kalisindh TPS Complex) leading to tripping of 660 MW Chhabra SCTPS unit-2. vi)As per PMU at Bhiwani(PG), B-N phase to earth fault followed by B-N phase to earth fault with unsuccessful A/R again followed by Y-N phase to earth fault was observed with fault clearing time of | grid_india_gd/grid_events/2026-04-01
G00190 | 2026-04 | 4 | GI-2 | Haryana | HR | Northern | 2026-04-04T19:21 | 2026-04-04T23:31 | 4.17 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Haryana 04-04-2026 19:21 04-04-2026 23:31 04:10 0 0 0.00% 0.00% 49166 56823 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 2000 MW power from Champa to Kurukshetra (500 MW on each Pole as per SCADA). ii)As reported, at 19:20:50.946 hrs, a DC line fault was det | 4 GI-2 Haryana 04-04-2026 19:21 04-04-2026 23:31 04:10 0 0 0.00% 0.00% 49166 56823 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 2000 MW power from Champa to Kurukshetra (500 MW on each Pole as per SCADA). ii)As reported, at 19:20:50.946 hrs, a DC line fault was detected at 363.35 km from Kurukshetra (Tower No. 2483, 2482 & 2481). Control started a restart aƩempt to mitigate the fault, and the fault was successfully cleared. iii)Subsequently, at 19:20:57.363 hrs, the DC line fault reoccurred. The restart sequence was again started and the fault was cleared. iv)However, at 19:21:08.788 hrs, the DC line fault occurred for the third time. Control once again aƩempted the restart sequence, but due to the persistent nature of the fault and exhaustion of all restart attempts, 800 KV HVDC Kurukshetra(PG) Pole-2 & 4 were eventually blocked. During line patrolling, no abnormality was seen on the line. v)As per PMU at Kurukshetra (PG), two consecutive R-Y-B-N three phase to earth faults were observed with fault clearing time of 120 msec. vi)As per SCADA, no change in demand in Haryana control area and no change in power order was observed. The power order of Pole-1 & 3 ramped up to compensate the Power of Pole 2 & 4. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 | grid_india_gd/grid_events/2026-04-01
G00191 | 2026-04 | 40 | GI-2 | Telangana | TG | Southern | 2026-04-04T22:26 | 2026-04-05T18:26 | 20 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-2 TELANGANA 04-04-2026 22:26 05-04-2026 18:26 20:00 0 0 0.0 % 0.0 % 48715.94 56825.5 Tripping of 400kV Bus-2 at Dichipally of TGTRANSCO The triggering incident is the R-G Bus fault in 400 kV Bus-2 due to bus post insulator failure leading to Bus Bar protection Operation and leading to the trip | 12 GI-2 TELANGANA 04-04-2026 22:26 05-04-2026 18:26 20:00 0 0 0.0 % 0.0 % 48715.94 56825.5 Tripping of 400kV Bus-2 at Dichipally of TGTRANSCO The triggering incident is the R-G Bus fault in 400 kV Bus-2 due to bus post insulator failure leading to Bus Bar protection Operation and leading to the tripping of 400kV Bus-2 at Dichipally due to inclement weather conditions. 400 kV Dichipally-Nirmal line and 400 kV/220 kV Dichipally ICT-4 got tripped during the event. 400KV-DICHPALLY-NIRMAL-1, 400KV/220KV DICHPALLY-ICT-4, DICHPALLY - 400KV - Bus 2 | grid_india_gd/grid_events/2026-04-01
G00192 | 2026-04 | 43 | GD-1 | Odisha | OD | Eastern | 2026-04-06T16:03 | 2026-04-06T16:09 | 0.1 | 810 | 670 | FALSE | FALSE | FALSE | FALSE | FALSE | 400kV JSPL and ACPP-II became dead and generation loss of 410 MW and 400 MW reported at JSPL and ACPP-II respectively. | 2 GD-1 Odisha 06-04-2026 16:03 06-04-2026 16:09 00:06 810 670 3.16% 2.56% 25631 26214 Prior to the event around 600 MW generation of JSPL and 400 MW generation of ACPP-II with 140 MW export to grid through JSPL-Meramundali D/C line. At 16:03 Hrs on 06/04/2026, 400 kV Meramundali-JSPL-1 line tripped from JSPL end due B-phase CT blast at JSPL end. At the same time 400 kV Meramundali-JSPL-2 line tripped on Z- 4 protection from JSPL end only, which led to island formation of JSPL unit-1 with emergency load and remaining JSPL units and load with ACPP-II form another island which was not survive due to load generation mismatch. 400kV JSPL and ACPP-II became dead and generation loss of 410 MW and 400 MW reported at JSPL and ACPP-II respectively. Total net load loss at JSPL was 670 MW. 400 kV JSPL-Meeramundali-1 400 kV JSPL-Meeramundali-2 | grid_india_gd/grid_events/2026-04-01
G00193 | 2026-04 | 6 | GD-1 | Uttarakhand | UK | Northern | 2026-04-09T02:13 | 2026-04-09T03:23 | 1.17 | 23 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | x)As per SCADA, generation loss of approx 23 MW was observed at Tanakpur HEP(NH). | 6 GD-1 Uttarakhand 09-04-2026 02:13 09-04-2026 03:23 01:10 23 0 0.06% 0.00% 35820 39271 i)During antecedent condition, 31.4 MW Tanakpur(NH) Unit-1 & 3 were only in running condition and generating approx 13 MW and 10 MW respectively. ii)As reported, at 02:13hrs, 220 KV Tanakpur(NH)-CBGanj(UP) (PG) Ckt tripped on R-N phase to earth fault (exact reason, nature and location of fault yet to be shared). iii)During the same time, busbar differential (zone-A) protection operated due to improper feedback status of the Bus isolator for 220 KV Tanakpur(NH)-CBGanj(UP) (PG) Ckt and tripped all elements connected to 220kV Bus-1 at Tanakpur(NH). iv)Due to the non-availability of power evacuation path, 31.4 MW Tanakpur(NH) Unit-3 connected to Bus-2 also tripped because of sudden load throw-off and complete blackout occurred at 220/132kV Tanakpur HEP(NH) S/s. v)As per DR, Busbar differential current of ~122 A was present before the event (persisting Id alarm) which matched the load current of 220 KV Tanakpur(NH)-CBGanj(UP) (PG) Ckt. vi)After investigation, it was found that “Switch Alarm” and “ZA ID Alarm” signals were active prior to the incident and feedback status of the Bus isolator for 220 KV Tanakpur(NH)-CBGanj(UP) (PG) Ckt was improper. vii)As a result, when R-N phase to earth fault occurred on 220 KV Tanakpur(NH)-CBGanj(UP) (PG) Ckt, R-phase current increased to 816 A, which was reflected as differential current in the R-phase of ZA busbar relay as per existing relay configuration. v | grid_india_gd/grid_events/2026-04-01
G00194 | 2026-04 | 5 | GD-1 | Delhi | DL | Northern | 2026-04-09T14:30 | 2026-04-10T13:40 | 23.17 | 0 | 216 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GD-1 Delhi 09-04-2026 14:30 10-04-2026 13:40 23:10 0 216 0.00% 0.56% 52436 38802 i)400/220/66kV Harsh Vihar(DV) has double main Bus scheme at both 400kV and 220kV side. ii)During antecedent condition, 400 KV Dadri(NT)-Loni Harsh Vihar(DV) (NT) Ckt-1 & 2 were connected to 400kV Harsh Vihar and the | 5 GD-1 Delhi 09-04-2026 14:30 10-04-2026 13:40 23:10 0 216 0.00% 0.56% 52436 38802 i)400/220/66kV Harsh Vihar(DV) has double main Bus scheme at both 400kV and 220kV side. ii)During antecedent condition, 400 KV Dadri(NT)-Loni Harsh Vihar(DV) (NT) Ckt-1 & 2 were connected to 400kV Harsh Vihar and the supply was further extended to 220kV Preet Vihar, Patparganj, I.P. Stn, Rajghat, Pragati and GTPS. iii)As reported, at 14:30hrs, 400 KV Dadri(NT)-Loni Harsh Vihar(DV) (end) (NT) Ckt-1 tripped on B-N phase to earth fault with fault current of ~5.623 kA (as per DR) from Loni Harsh Vihar end. As per DR, fault sensed in zone-1 at Loni Harsh Vihar end, A/R operated but was unsuccessful as fault was of permanent nature. iv)During the same time, 400 KV Dadri(NT)-Loni Harsh Vihar(DV) (end) (NT) Ckt-2 also tripped sensing this fault (as per DR, fault current sensed ~4.773kA from Loni Harsh Vihar end) from Dadri(NT) end only, no tripping occurred at Harsh Vihar(DV) end (exact nature of protection operation yet to be shared). v)Due to tripping of both 400 KV Dadri(NT)-Loni Harsh Vihar(DV) (NT) Ckt-1 & 2, supply failed at 220kV level and complete blackout occurred at 400/220/66kV Harsh Vihar(DV) S/s. vi)As per PMU at Dadri(NT), B-N phase to earth fault with unsuccessful A/R was observed with fault clearing time of 80 ms. vii)As per SCADA, change in demand of ~330 MW in Delhi control area is observed. However, as reported by SLDC Delhi load loss of ~216 MW occurred in Delhi control area. Load o | grid_india_gd/grid_events/2026-04-01
G00195 | 2026-04 | 29 | GI-2 | Gujarat | GJ | Western | 2026-04-11T04:04 | 2026-04-11T04:35 | 0.52 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | As both the units of Vadinar are under RSD, there was no generation loss at Essar Vadinar. | 3 GI-2 Gujarat 11-04-2026 04:04 11-04-2026 04:35 00:31 - - - - 77718 63470 Partial outage of 400kV (Essar) Vadinar S/S: At 04:01/11-04-2026, 400 kV Vadinar-Kalwad-1 tripped on O/V stage-1 operation from Kalwad end and DT received at Essar Vadinar resulting in complete blackout at 400 kV Essar Vadinar S/S. Prior to the event, 400kV Vadinar-Kalwad 2 was under forced outage since 06 Feb’26 due to GIS issue at Kalwad endand 400kV Vadinar-Amreli 1&2 were already out of service on voltage regulation. As both the units of Vadinar are under RSD, there was no generation loss at Essar Vadinar. 1. 400KV-AMRELI-VADINAR-2 2. 400KV-VADINAR-BUS-1 3. 400KV-VADINAR-BUS-2 | grid_india_gd/grid_events/2026-04-01
G00196 | 2026-04 | 30 | GI-1 | Maharashtra | MH | Western | 2026-04-13T04:45 | 2026-04-13T05:10 | 0.42 | 31 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-1 Maharashtra 13-04-2026 04:45 13-04-2026 05:10 00:25 31 - 0.04% - 78221 64366 Partial outage of 220 kV Boisar (MSETCL): At 04:45 hrs / 13-04-2026, Zone-1 R-B phase to phase fault occurred in 220 kV Boisar(MH)-Palghar-1 S/C at Boisar(MH) end. Part of 220 kV Boisar(MH)-Kudus-1 S/C is under outag | 4 GI-1 Maharashtra 13-04-2026 04:45 13-04-2026 05:10 00:25 31 - 0.04% - 78221 64366 Partial outage of 220 kV Boisar (MSETCL): At 04:45 hrs / 13-04-2026, Zone-1 R-B phase to phase fault occurred in 220 kV Boisar(MH)-Palghar-1 S/C at Boisar(MH) end. Part of 220 kV Boisar(MH)-Kudus-1 S/C is under outage for reconductoring and other part is charged as 220 kV Boisar(MH)-Palghar-1 S/C by bunching arrangement at tower location 11. B phase of pole of the 220 kV Boisar(MH)-Palghar-1 S/C at Boisar(MH) failed to open (zero SF-6 pressure was recorded (as per realtime information provided by SLDC Maharashtra)). Due to non-operation of B phase pole LBB protection operated, resulting in tripping of 220 kV Boisar(MH)-Bus-1 (Double main and transfer bus scheme) and all connected elements. Due to high fault current R phase wave trap uncoiled and failed and B phase jumper between 220 kV Boisar(MH)-Bus-1 and 220 kV Boisar(MH)-Bus-2 disconnected. Load loss of 30.55 MW occurred at Boisar(MH) area due to the event. 1. 220kV Boisar(MH) Bus-1 2. 220kV Boisar(MH)-Boisar(PG)-2 3. 220kV Boisar(MH)-Tarapur(I) 4. 220kV Boisar(MH)-Palghar 5. 220kV Boisar(MH)-Viraj 6. 200MVA 220/132kV Boisar(MH) ICT-2 7. 80MVA 220/33kV Power Transformer-1 8. 220kV Bus coupler | grid_india_gd/grid_events/2026-04-01
G00197 | 2026-04 | 31 | GI-2 | Gujarat | GJ | Western | 2026-04-13T11:07 | 2026-04-13T14:23 | 3.27 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GI-2 Gujarat 13-04-2026 11:07 13-04-2026 14:23 03:16 - - - - 82037 72784 Partial outage of 400kV Kalavad S/S:At 11:08 hrs /13-04-2026, 400 kV Bus-1 tripped at the 400 kV Kalavad GIS substation on Bus bar protection operation. Prior to the event, 400kV Kalavad Hadala 1 & 2 were under planned outage | 5 GI-2 Gujarat 13-04-2026 11:07 13-04-2026 14:23 03:16 - - - - 82037 72784 Partial outage of 400kV Kalavad S/S:At 11:08 hrs /13-04-2026, 400 kV Bus-1 tripped at the 400 kV Kalavad GIS substation on Bus bar protection operation. Prior to the event, 400kV Kalavad Hadala 1 & 2 were under planned outage. 400kV Kalavad Vadinar 2 was under forced outage. 400/220 kV ICT-2 was out due to LA failure. During shutdown, maintenance work of bus 1 gas density meter, chattering of the G2 gas contactor in the Hadala line bay was observed. While troubleshooting this issue, the DC positive supply to the G1 gas contactor got disconnected due to manual error. Consequently, as per the SF₆ gas lockout scheme, a Bus-1 gas zone trip command was initiated, resulting in the tripping of all elements connected to the 400 kV Bus-1 i.e. ICT-1, Bhogat-1 and Vadinar-1 and hence complete blackout of 400/220 kV Kalwad S/S as Bus-2 is already under shutdown. Lines didn’t trip at remote end as DT signal was not configured in BBP scheme. No load loss was reported due to the event. 1. 400kV Kalavad Bhogat 1 2. 400kV Kalavad Vadinar 1 3. 400kV Kalavad Bus 1 4. 400kV Kalavad Bus 2 5. 400/220 KV Kalavad ICT-1 | grid_india_gd/grid_events/2026-04-01
G00198 | 2026-04 | 8 | GD-1 | Uttarakhand | UK | Northern | 2026-04-13T12:49 | 2026-04-13T13:35 | 0.77 | 0 | 380 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GD-1 Uttarakhand 13-04-2026 12:49 13-04-2026 13:35 00:46 0 380 0.00% 0.92% 54095 41385 i)400/220KV Kashipur(UK) has one and half bus scheme at 400kV level and double main transfer bus scheme at 220kV level. There are 2*315 MVA ICTs at Kashipur and SPS has also been in service at Kashipur in view o | 8 GD-1 Uttarakhand 13-04-2026 12:49 13-04-2026 13:35 00:46 0 380 0.00% 0.92% 54095 41385 i)400/220KV Kashipur(UK) has one and half bus scheme at 400kV level and double main transfer bus scheme at 220kV level. There are 2*315 MVA ICTs at Kashipur and SPS has also been in service at Kashipur in view of N-1 non-complaint ICTs. ii)During antecedent condition, 400/220kV 2*315 MVA ICTs at Kashipur were in service and carrying approx 129 MW each (as per SCADA). iii)As reported, at 12:49 hrs, Y-B phase to phase fault occurred on 220kV Kashipur-Jafarpur Ckt. Fault occurred due to conductor snapping at Tower No. 12 (~6 km from Kashipur and ~49.24 km from Jafarpur end). fault was detected in zone-1 by the distance relays at both ends. At the Jafarpur end, the breaker tripped successfully. However, at the Kashipur end, although the Main-2 distance relay detected the fault and issued a trip command, the breaker failed to operate, resulting in non-clearance of the fault from Kashipur end. Main-1 relay was already out of service prior to the incident. iv)Further, as fault was still persisting, after approximately 640 ms (as per PMU), the fault converted to 3-phase fault due to involvement of the remaining phase (R-ph) at Tower No. 17 and Tower No. 18 (as reported). v)The fault continued till another 1280 ms (as per PMU) and 220kV Kashipur-Pantnagar Ckt and 220 KV Pantnagar(UK)-Bareilly(UP) (UP) Ckt tripped from Pantnagar and Bareilly end respectively in zone-3 and 400/220kV 315 MVA ICT-1 & | grid_india_gd/grid_events/2026-04-01
G00199 | 2026-04 | 7 | GI-2 | Delhi | DL | Northern | 2026-04-13T15:14 | 2026-04-13T16:22 | 1.13 | 0 | 143 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GI-2 Delhi 13-04-2026 15:14 13-04-2026 16:22 01:08 0 143 0.00% 0.35% 53155 40821 i)400/220/66kV Harsh Vihar(DV) has double main Bus scheme at both 400kV and 220kV side. ii)During antecedent condition, 400/220 kV 315 MVA ICT 2 & 3 at Loni Harsh Vihar(DV) were in service and carrying approx 175 MW e | 7 GI-2 Delhi 13-04-2026 15:14 13-04-2026 16:22 01:08 0 143 0.00% 0.35% 53155 40821 i)400/220/66kV Harsh Vihar(DV) has double main Bus scheme at both 400kV and 220kV side. ii)During antecedent condition, 400/220 kV 315 MVA ICT 2 & 3 at Loni Harsh Vihar(DV) were in service and carrying approx 175 MW each (as per SCADA) feeding the load of 220kV Harsh Vihar, Preet Vihar, I.P. Stn, Rajghat and GTPS. iii)As reported, as per the instructions received vide MoM dated 24.02.2026 of 11th Delhi OCC Meeting, the work of installation of System Protection Scheme (SPS) is under progress for past 20 days at 400/220/66kV Harsh Vihar(DV) S/s. iv)As per DR, at 15:14 hrs, 400/220 kV 315 MVA ICT 2 & 3 at Loni Harsh Vihar(DV) tripped on Directional O/C protection operation; however no increase in phase currents was observed (suspected maloperation). v)As per PMU at Dadri(NT), no fault was observed in the system; however voltage dip was observed in all 3 phases. vi)As per SCADA, change in demand of ~79 MW in Delhi control area is observed. However, as reported by SLDC Delhi load loss of ~143 MW occurred in Delhi control area. As reported, at 15:21hrs, 220kV Bus Coupler was made ON at 220kV Pragati Stn and total load was normalized. 1) 400/220 kV 315 MVA ICT 2 at Loni Harsh Vihar(DV) 2) 400/220 kV 315 MVA ICT 3 at Loni Harsh Vihar(DV) | grid_india_gd/grid_events/2026-04-01
G00200 | 2026-04 | 9 | GD-1 | Rajasthan | RJ | Northern | 2026-04-15T18:52 | 2026-04-15T19:36 | 0.73 | 0 | 320 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GD-1 Rajasthan 15-04-2026 18:52 15-04-2026 19:36 00:44 0 320 0.00% 0.53% 50724 60802 i)220/132kV Kushkhera(RS) has double main bus scheme at 220kV level. ii)During antecedent condition, 220kV Neemrana(PG)-Kushkhera(RS) (RS) Ckt and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt were carrying 125 MW & 1 | 9 GD-1 Rajasthan 15-04-2026 18:52 15-04-2026 19:36 00:44 0 320 0.00% 0.53% 50724 60802 i)220/132kV Kushkhera(RS) has double main bus scheme at 220kV level. ii)During antecedent condition, 220kV Neemrana(PG)-Kushkhera(RS) (RS) Ckt and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt were carrying 125 MW & 197 MW respectively. iii)As reported, at 18:42 hrs, R-N fault occured on 220 KV Neemrana (PG)-Kushkhera(RS) (RS) Ckt due to burnt/ damaged CT at Kushkhera end with fault distance of 58.8 km from Neemrana(PG) end; fault sensed in zone-2 at Neemrana end. iv)As per DR, 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt sensed this fault in zone-4 at Kushkhera(RS) end with fault current of ~12.388kA from Kushkhera(RS) end. 220 KV Neemrana(PG)-Kushkhera(RS) (RS) ckt sensed this fault in zone-1 first, however after some time zone-4 picked up at Kushkhera(RS) end with fault current of ~16.916kA from Kushkhera(RS) end. v)On this fault, bus bar protection operated at both 220kV buses of Kushkhera(RS) which led to tripping of all the elements connected at 220kV Kushkhera(RS) and complete blackout occurred at i)220/132kV Kushkhera(RS) S/s. (Reason of tripping of both the 220kV buses yet to be received). vi)As per PMU at Bhiwadi(PG), R-N phase to earth fault was observed with fault clearing time of 80ms. vii)As per SCADA, change in demand of ~320 MW in Rajasthan control area is observed. 1) 220 KV Neemrana(PG)-Kushkhera(RS) (RS) ckt 2) 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt 3) 220 KV Kushkhera(RS)-Ka | grid_india_gd/grid_events/2026-04-01
G00201 | 2026-04 | 11 | GI-2 | Punjab | PB | Northern | 2026-04-16T12:00 | 2026-04-16T13:57 | 1.95 | 0 | 96 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-2 Punjab 16-04-2026 12:00 16-04-2026 13:57 01:57 0 96 0.00% 0.19% 58954 49837 i)400/220kV Nakodar(PS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)As reported, at 12:00 hrs, bus fault occurred due to bus isolator sparking at Nakodar | 11 GI-2 Punjab 16-04-2026 12:00 16-04-2026 13:57 01:57 0 96 0.00% 0.19% 58954 49837 i)400/220kV Nakodar(PS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. ii)As reported, at 12:00 hrs, bus fault occurred due to bus isolator sparking at Nakodar end of 220kV Nakodar-Ladowal Ckt-2 during shutdown work (exact nature and location of fault yet to be shared). On this bus fault, bus bar protection at 220kV Nakodar(PS) failed to operate. iii)Due to non-clearance of fault, all 220kV lines connected at Nakodar(PS) tripped from remote end on zone-2 distance protection operation and 400/220 kV 315 MVA ICT 1 & 2 and 500 MVA ICT 3 at Nakodar(PS) tripped on directional over-current protection operation. iv)As per PMU at Moga(PG), Y-N Phase to earth fault converted to 3 phase to earth fault was observed with delayed fault clearing time of 2520ms. v)As per SCADA, change in demand of approx 96 MW was observed in Punjab control area. 1) 400/220 kV 315 MVA ICT 1 at Nakodar(PS) 2) 400/220 kV 315 MVA ICT 2 at Nakodar(PS) 3) 400/220 kV 500 MVA ICT 3 at Nakodar(PS) 4) 220 kV Nakodar-Kartarpur Ckt-1 5) 220 kV Nakodar-Kartarpur Ckt-2 6) 220 kV Nakodar-Hoshiarpur Ckt 7)220 kV Nakodar-Rihana Jatta Ckt 8) 220 kV Nakodar-Nurmahal Ckt-1 9) 220 kV Nakodar-Nurmahal Ckt-2 10) 220kV Nakodar-Ladowal Ckt-1 11) 220kV Nakodar-Ladowal Ckt-2 | grid_india_gd/grid_events/2026-04-01
G00202 | 2026-04 | 10 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-04-16T22:02 | 2026-04-17T00:21 | 2.32 | 0 | 72 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Jammu and Kashmir 16-04-2026 22:02 17-04-2026 00:21 02:19 0 72 0.00% 0.12% 54370 62581 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 and 220 KV Chowadhi(JK)-Jammu(PDD) (JK) Ckt w | 10 GD-1 Jammu and Kashmir 16-04-2026 22:02 17-04-2026 00:21 02:19 0 72 0.00% 0.12% 54370 62581 i)220/132/33kV Jammu/Gladni(J&K) S/s have double main bus arrangement at 220kV side. ii)During antecedent condition, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 and 220 KV Chowadhi(JK)-Jammu(PDD) (JK) Ckt were carrying 32 MW, 28 MW and 20 MW respectively (as per SCADA). iii)As reported, at 22:02 hrs, 220kV R-ph CT of Bus coupler bay at Jammu/ Gladni(JK) blasted. During the same time, 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 and 220 KV Chowadhi(JK)-Jammu(PDD) (JK) Ckt tripped and complete blackout occurred at 220/132/33kV Jammu/Gladni(J&K) S/s (exact nature and location of fault yet to be shared). iv)As per DR at Jammu/Gladni(JK) end, R-N phase to earth fault converted to 3-phase to earth fault occurred. Fault current was Ir=~2.946kA, Iy=~3.026kA, Ib=~2.642kA from Jammu end for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 and Ir=~2.678kA, Iy=~2.821kA, Ib=~2.504kA from Jammu end for 220 KV Salal(NH)- Jammu(PDD) (PG) Ckt-2. Fault sensed in zone-4 at Jammu end. Fault clearing time was ~720 ms and ~540 ms for 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 & 2 respectively. v)As per PMU at Kishenpur(PG), R-N phase to earth fault converted to 3-phase to earth fault with delayed fault clearing time of 720ms. vi)As per SCADA, change in demand of approx 72 MW was observed in J&K control area. 1) 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-1 2) 220 KV Salal(NH)-Jammu(PDD) (PG) Ckt-2 3) 220 KV Chowadhi(JK)-Jammu(P | grid_india_gd/grid_events/2026-04-01
G00203 | 2026-04 | 13 | GI-1 | Punjab | PB | Northern | 2026-04-17T04:25 | 2026-04-17T06:24 | 1.98 | 0 | 310 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GI-1 Punjab 17-04-2026 04:25 17-04-2026 06:24 01:59 0 310 0.00% 0.54% 46620 56935 i)220/132/66kV Jamalpur(BB) has double main Bus arrangement at 220kV side. 220KV Bus 2 at Jamalpur(BB) have two sections Bus-2A and 2B connected through Bus sectionalizer. ii)As reported, at 04:25 hrs, B-ph Coupling | 13 GI-1 Punjab 17-04-2026 04:25 17-04-2026 06:24 01:59 0 310 0.00% 0.54% 46620 56935 i)220/132/66kV Jamalpur(BB) has double main Bus arrangement at 220kV side. 220KV Bus 2 at Jamalpur(BB) have two sections Bus-2A and 2B connected through Bus sectionalizer. ii)As reported, at 04:25 hrs, B-ph Coupling capacitor of 220 KV Jalandhar-Jamalpur (BB) Ckt-1 got damaged which eventually led to bus bar protection operation at 220kV Bus-1 at Jamalpur(BB) (exact reason of busbar protection operation yet to be shared). iii)Due to this, all the elements connected to 220kV Bus-1 at Jamalpur(BB) tripped and Bus-1 became dead. iv)As per DR, R-N phase to earth fault occurred on 220 KV Jalandhar-Jamalpur (BB) Ckt-2 and fault sensed in zone-2 at Jalandhar end and carrier received from Jamalpur end indicating line fault on which A/R operated however became unsuccessful due to permanent nature of fault (exact reason, nature and location of fault yet to be shared). v)As per PMU at Bhakra(BB), B-N phase to earth fault immediately followed by Y-N phase to earth fault followed by R-N phase to earth fault with unsuccessful A/R again followed by Y-N phase to earth was observed with fault clearance time of 80ms, 120ms, 80ms, 120ms & 120ms respectively. vi)As per SCADA, change in demand of approx 310 MW was observed in Punjab control area. 1)220KV Bus 1 at Jamalpur(BB) 2)220 KV Jamalpur(BB)-Sangrur(BB) (BBMB) Ckt-1 3)220 KV Bhakra_R-Jamalpur (BB) Ckt-1 4)220 KV Jalandhar-Jamalpur (BB) Ckt-1 5)220 KV Jaland | grid_india_gd/grid_events/2026-04-01
G00204 | 2026-04 | 12 | GI-2 | Haryana | HR | Northern | 2026-04-17T05:08 | 2026-04-17T05:58 | 0.83 | 0 | 550 | FALSE | FALSE | FALSE | FALSE | FALSE | 1)400/220kV 315 MVA ICT-1 at Daulatabad(HR) 2)400/220kV 315 MVA ICT-3 at Daulatabad(HR) 3)400/220kV 315 MVA ICT-4 at Daulatabad(HR) 4)220 kV Daulatabad(HR)-Majra Ckt-1 5)220 kV Daulatabad(HR)-Majra Ckt-2 6)220 kV Daulatabad(HR)-Manesar Ckt 7)220 kV Daulatabad(HR)-Gurgaon Sec95 Ckt-1 8)220 kV Daulatabad(HR)-Gurgaon Sec95 Ckt-2 9)220 kV Daulatabad(HR)-Gurgaon Sec85 Ckt 10)220/66kV 100 MVA ICT-1 at D | 12 GI-2 Haryana 17-04-2026 05:08 17-04-2026 05:58 00:50 0 550 0.00% 0.96% 46400 57336 i)400/220kV Daulatabad(HR) has one & half breaker scheme at 400kV level and double main bus scheme at 220kV level. ii)During antecedent condition, 400/220kV 315 MVA ICT-1, 3 & 4 at Daulatabad(HR) were carrying 139 MW, 140 MW & 137 MW respectively. 400/220kV 315 MVA ICT-2 at Daulatabad(HR) was out of service. iii)As reported, at 05:08 hrs, 220kV B-ph CT and B-ph CB pole of 220/66kV 100 MVA ICT-2 at Daulatabad(HR) got damaged resulting into 220kV bus fault. iv)As bus bar protection was out of circuit at that time due to internal fault of Sifang relay, bus bar protection didn’t operate and fault cleared with the tripping of all three 400/220kV 315 MVA ICTs in service at Daulatabad(HR). v)All 220kV lines connected at Daulatabad(HR) tripped on either zone-4 from Daulatabad end or zone-2 from remote end (details yet to be confirmed). vi)As per PMU at Gurgaon(PG), B-N Phase to earth fault followed by another B-N Phase to earth fault converted to Y-B-N double phase to earth fault with fault clearing time of 80 ms and 640 ms (delayed) was observed. vii)As per SCADA change in demand of approx 550 MW in Haryana control area is observed. viii)As reported, Bus bar protection (Sifang) at 220kV Daulatabad(HR) was made healthy after replacement of defective CPU-2 card on 18.03.26. 1)400/220kV 315 MVA ICT-1 at Daulatabad(HR) 2)400/220kV 315 MVA ICT-3 at Daulatabad(HR) 3)400/220kV 315 MVA ICT-4 at Daulatabad( | grid_india_gd/grid_events/2026-04-01
G00205 | 2026-04 | 14 | GD-1 | Uttar Pradesh | UP | Northern | 2026-04-17T05:23 | 2026-04-17T07:15 | 1.87 | 0 | 70 | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GD-1 Uttar Pradesh 17-04-2026 05:23 17-04-2026 07:15 01:52 0 70 0.00% 0.12% 46504 56307 i)220/132kV Nara(UP) has single main and transfer Bus arrangement at both 220kV and 132 kV level. ii)During antecedent condition, 220kV Nara(UP)-Muzaffarnagar (UP) Ckt was charged through transfer bus at Nara( | 14 GD-1 Uttar Pradesh 17-04-2026 05:23 17-04-2026 07:15 01:52 0 70 0.00% 0.12% 46504 56307 i)220/132kV Nara(UP) has single main and transfer Bus arrangement at both 220kV and 132 kV level. ii)During antecedent condition, 220kV Nara(UP)-Muzaffarnagar (UP) Ckt was charged through transfer bus at Nara(UP) end. iii)As reported, at 05:23 hrs, B-ph CT of 220 KV Jansath-Meerut (PMSTL) Ckt at Jansath end damaged got damaged. As per DR, B-N phase to earth fault (Ib=~10.78kA) followed by Y-N phase to earth fault (Iy=~4.025kA) after ~564 ms was observed at Jansath end of 220 KV Jansath-Meerut (PMSTL) Ckt; reverse zone picked up at Jansath end. iv)As per DR of 220kV Jansath-Muzaffarnagar Ckt, B-N phase to earth fault (Ib=~7.14kA) followed by R-N phase to earth fault (Iy=~7.22kA) was observed at Jansath end; reverse zone picked up at Jansath end; B-phase pole of CB auto-reclosed at Muzaffarnagar end. v)As per DR of 220kV Nara(UP)-Muzaffarnagar (UP) Ckt, B-N phase to earth fault (Ib=~821A) followed by R-N phase to earth fault (Iy=~1.67kA) after ~564 ms was observed at Nara end. Zone-3 picked up at Nara end on R-N fault and later backup directional O/C E/F (IN>2) protection operated. However due to damaged tripping wiring of transfer bus-coupler bay and delayed opening of CBs, LBB protection operated after 200 ms at Nara end. vi)Due to LBB operation at Nara(UP) end, all 220kV lines connected at Nara(UP) along with 220/132kV ICTs at Nara(UP) tripped and complete blackout occurred at 220/132k | grid_india_gd/grid_events/2026-04-01
G00206 | 2026-04 | 32 | GD-1 | Maharashtra | MH | Western | 2026-04-17T16:15 | 2026-04-17T16:40 | 0.42 | 649 | 336 | FALSE | FALSE | FALSE | FALSE | FALSE | The disturbance led to a total generation loss of 645 MW and an associated load loss of 503 MW, as reported. | 6 GD-1 Maharashtra 17-04-2026 16:15 17-04-2026 16:40 00:25 649 336 0.69% 0.43% 93459 77874 Complete outage of 400 kV Khaperkheda S/S (MSETCL):At 16:15 hrs/17-04-2026, both 220 kV Bus-I and Bus-II tripped on busbar differential protection following a B- phase potential transformer (PT) failure on Bus-I. The busbar protection operated correctly, resulting in the tripping of all connected 220 kV feeders, as well as 400 kV ICT-1 and ICT-2. Subsequently, due to the loss of the evacuation path, generating Units 1, 2, 3, and 4 (210 MW each) tripped on protection. The disturbance led to a total generation loss of 645 MW and an associated load loss of 503 MW, as reported. 1. 220 KV Bus 1 2. 220 KV Bus 2 3. 400/220 KV ICT 1 4. 400/220 KV ICT 2 5. 220 KV Khaparkheda Khaparkheda D/C 6. 220 KV Khaparkheda Bhandara 1 & 2 7. 220 KV Khaparkheda Koradi 8. 220 KV Khaparkheda Kalmeshwar 9. 220 KV Khaparkheda Butibori 1 & 2 10. 220 KV Khaparkheda Kanhan 11. 220 KV Khaparkheda Ambazari 10. Khaparkheda Unit 1,2,3,4 (210 MW) Elements Tripped Details of Grid Events during the Month of April 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditi | grid_india_gd/grid_events/2026-04-01
G00207 | 2026-04 | 16 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-04-18T00:16 | 2026-04-18T01:55 | 1.65 | 0 | 158 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GI-1 Jammu and Kashmir 18-04-2026 00:16 18-04-2026 01:55 01:39 0 158 0.00% 0.27% 50155 58548 i)400/220kV Wagoora(PG) has double main and transfer Bus arrangement at both 400KV and 220KV side. 220/132kV Pampore(J&K) has double bus scheme at 220kV level however SCADA data is not healthy there. ii)D | 16 GI-1 Jammu and Kashmir 18-04-2026 00:16 18-04-2026 01:55 01:39 0 158 0.00% 0.27% 50155 58548 i)400/220kV Wagoora(PG) has double main and transfer Bus arrangement at both 400KV and 220KV side. 220/132kV Pampore(J&K) has double bus scheme at 220kV level however SCADA data is not healthy there. ii)During antecedent condition, power flow from Wagoora(PG) S/s to Pampore(PDD) S/s was approx 170 MW (85 MW each) through 220 KV Wagoora(PG)- Pampore(PDD) (PG) D/C. Load of 220/132kV Pampore(J&K) was being fed from Wagoora only. iii)As reported at 00:16 hrs, 220kV Wagoora(PG)-Pampore(PDD) (PG) Ckt-1 & 2 tripped from Wagoora end on B-N phase to earth fault in Z-2. Fault distance was ~11km from Wagoora end and fault current was ~6kA. iv)As per PMU at Amargarh(INDIGRID), B-N phase to earth fault clearing time of 160ms is observed. v)Due to tripping of both the lines, load of 220/132kV Pampore(J&K) affected. As per SCADA, change in demand of approx 158 MW is observed in J&K control area. 1)220 KV Wagoora(PG)-Pampore(PDD) (PG) Ckt-1 2)220 KV Wagoora(PG)-Pampore(PDD) (PG) Ckt-2 | grid_india_gd/grid_events/2026-04-01
G00208 | 2026-04 | 15 | GD-1 | Rajasthan | RJ | Northern | 2026-04-18T11:23 | 2026-04-18T11:30 | 0.12 | 504 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | viii)As per SCADA, generation loss of approx 244 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 260 MW was observed. | 15 GD-1 Rajasthan 18-04-2026 11:23 18-04-2026 11:30 00:07 504 0 1.13% 0.00% 44776 52540 i)220kV Barsingsar(NLC) has double main and transfer bus scheme at 220kV level. ii)During antecedent condition, 125 MW Barsingsar(NLC) - Unit 1 & 2 were generating approx 122 MW each. iii)As reported, at 11:23 hrs, 220 kV Barsingsar(NLC)-Nagaur (RS) Ckt tripped on Y-N phase to earth fault with fault distance of 54.6 km and fault current of 1.47kA from Nagaur end; fault sensed in zone-1 at Nagaur end. iv)During the same time, 220 kV Barsingsar-Bikaner(RS) Ckt, 220 kV Barsingsar(NLC)-Khinwsar (RS) Ckt, 220 kV Barsingsar(NLC)-Baap (RS) Ckt and 125 MW Barsingsar(NLC) - Unit 1 & 2 also tripped (exact reason of tripping along with nature of protection operation yet to be shared). v)As further reported, 220 kV Phalodi-Baap (RS) Ckt also tripped at the same time on 3-phase to earth fault (exact reason, nature and location of fault yet to be shared). vi)Due to this, complete blackout occurred at 220 kV Barsingsar(NLC) and 220/132/33kV Baap(RS) S/s. vii)As per PMU at Bhadla(PG), no fault was observed in the system; however fluctuation in voltage was present. viii)As per SCADA, generation loss of approx 244 MW occurred at Barsingsar(NLC) and change in Rajasthan solar generation of approx 260 MW was observed. 1)220 kV Barsingsar(NLC)-Nagaur (RS) Ckt 2)220 kV Barsingsar(NLC)-Bikaner Ckt 3)220 kV Barsingsar(NLC)-Khinwsar (RS) Ckt 4)220 kV Barsingsar(NLC)-Baap (RS) Ckt 5)125 MW Barsingsar(NLC) - Unit 1 6 | grid_india_gd/grid_events/2026-04-01
G00209 | 2026-04 | 17 | GI-1 | Uttarakhand | UK | Northern | 2026-04-18T16:43 | 2026-04-18T17:09 | 0.43 | 0 | 42 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-1 Uttarakhand 18-04-2026 16:43 18-04-2026 17:09 00:26 0 42 0.00% 0.08% 52842 55416 i)132/33kV Sitarganj(UK) S/s has main & transfer bus scheme and is connected with 220/132kV Sitarganj(PG) through 132kV Sitarganj(PG)-Sitarganj(UK) D/C. Both these lines having differential protection as main pr | 17 GI-1 Uttarakhand 18-04-2026 16:43 18-04-2026 17:09 00:26 0 42 0.00% 0.08% 52842 55416 i)132/33kV Sitarganj(UK) S/s has main & transfer bus scheme and is connected with 220/132kV Sitarganj(PG) through 132kV Sitarganj(PG)-Sitarganj(UK) D/C. Both these lines having differential protection as main protection and O/C E/F as back up protection at both the ends. ii)During antecedent condition, 132kV Sitarganj-Kichha (PTCUL) Ckt was already opened from Kichha end for rostering Purpose. iii)As reported, at 16:43hrs, Y-ph CT of 132kV Sitarganj(PG)-Sitarganj(UK) line-II at Sitarganj(UK) end damaged. 132kV Sitarganj(PG)-Sitarganj(UK) line-II tripped from both the ends on differential protection operation. iv)As the CT was on bus side, the fault came under bus fault zone and didn’t clear after tripping of 132kV Sitarganj(PG)-Sitarganj(UK) line-II. Within ~200mse of fault, Y- N fault converted into three phase fault. v)132kV Sitarganj(UK)-Pilibhit(UP) line and 132kV Sitarganj-Khatima(UK) line also tripped with delay of ~400msec on Z-2 distance protection operation. vi)Back up O/C E/F protection at Sitarganj(PG) end of 132kV Sitarganj(PG)-Sitarganj(UK) line-I didn’t operate and thus fault cleared after tripping of 220/132kV 100 MVA ICT-1, 2 & 3 on backup overcurrent protection operation within ~1.3sec. vii)220kV Tanakpur-Sitarganj line also tripped during the event. As reported, line tripped instantaneously after detecting fault in Z-3. viii)As per PMU at Bareilly(PG), Y-N fault converte | grid_india_gd/grid_events/2026-04-01
G00210 | 2026-04 | 33 | GD-1 | Maharashtra | MH | Western | 2026-04-19T18:55 | 2026-04-19T23:47 | 4.87 | 25 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 25 MW Occurred at Tuljapur (Renew Power) due to loss of evacuation path. | 7 GD-1 Maharashtra 19-04-2026 18:55 19-04-2026 23:47 04:52 25 - 0.03% - 80761 66077 Complete outage of 400 kV Tuljapur (Renew Power):At 18:55 hrs / 19-04-2026, 400 kV Konhali-Tuljapur-1 S/C tripped on R-E Fault in zone-1 at Konhali End. No abnormality was found during patrolling. Generation loss of 25 MW Occurred at Tuljapur (Renew Power) due to loss of evacuation path. 1. 400 kV Konhali-Tuljapur-1 | grid_india_gd/grid_events/2026-04-01
G00211 | 2026-04 | 44 | GD-1 | Jharkhand | JH | Eastern | 2026-04-19T23:13 | 2026-04-19T23:55 | 0.7 | 317 | 120 | FALSE | FALSE | FALSE | FALSE | FALSE | 400/220kV Tenughat S/s became dead and 317 MW generation loss reported at Tenughat S/s. | 3 GD-1 Jharkhand 19-04-2026 23:13 19-04-2026 23:55 00:42 317 120 0.96% 0.39% 32995 30910 At 23:13 Hrs on 19/04/2026, B-phase CT of bus coupler bay at Tenughat got burst which created bus fault at 220kV Tenughat S/s. Due to non-operation of bus bar protection at Tenughat S/s, all 220 kV emanating lines at Tenughat i.e., 220 kV Tenughat-Govindpur D/c and 220 kV Tenughat-Biharsharif got tripped from remote ends in Z-2. 400/220kV Tenughat S/s became dead and 317 MW generation loss reported at Tenughat S/s. This led to overloading of 220 kV Maithon-Dumka D/c and SPS operated at Dumka S/s. Load loss of around 120 MW occurred at Godda and Pakur due to SPS operation. 220KV-TENUGHAT-BIHARSHARIF 220KV-TENUGHAT-GOVINDPUR-1 220KV-TENUGHAT-GOVINDPUR-2 220KV-TENUGHAT MAIN BUS-1 220KV-TENUGHAT MAIN BUS-2 210 MWU#1 at Tenughat 210 MWU#2 at Tenughat 400/220 kV ICT-1 at Tenughat 400/220 kV ICT-2 at Tenughat | grid_india_gd/grid_events/2026-04-01
G00212 | 2026-04 | 18 | GD-1 | Uttar Pradesh | UP | Northern | 2026-04-20T01:29 | 2026-04-20T02:12 | 0.72 | 0 | 110 | FALSE | FALSE | FALSE | FALSE | FALSE | 1)220kV Phulpur(UP)-Pratapgarh Ckt 2)220 KV Allahabad(PG)-Phulpur(UP) (UP) Ckt-1 3)220 KV Phulpur(UP)-Jaunpur Ckt 4)220/132 kV 160 MVA ICT-1 at Phulpur (UP) 5)220/132 kV 160 MVA ICT-2 at Phulpur (UP) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events du | 18 GD-1 Uttar Pradesh 20-04-2026 01:29 20-04-2026 02:12 00:43 0 110 0.00% 0.18% 50547 61276 i)220/132kV Phulpur(UP) has single main and transfer Bus arrangement at both 220kV and 132 kV level (220kV Phulpur(UP)-Aurai Ckt is yet to be commissioned). ii)As reported, at 01:29 hrs, B-ph CT of 220kV Phulpur(UP)-Pratapgarh Ckt at Phulpur end got damaged. Fault was sensed in zone-1 at Phulpur end. iii)During the same time, bus bar protection operated at 220kV Bus at Phulpur(UP) and all the elements connected to the bus tripped. This led to complete blackout at 220/132kV Phulpur(UP). iv)As per PMU at Allahabad(PG), B-N phase to earth fault was observed with fault clearance time of 120ms. v)As per SCADA, change in demand of approx 110 MW was observed in UP control area. vi)As reported by SLDC UP , supply at 220kV Phulpur(UP) was normalised at 02:12 hrs via charging of 220kV Phulpur(UP)-Jaunpur Ckt. 1)220kV Phulpur(UP)-Pratapgarh Ckt 2)220 KV Allahabad(PG)-Phulpur(UP) (UP) Ckt-1 3)220 KV Phulpur(UP)-Jaunpur Ckt 4)220/132 kV 160 MVA ICT-1 at Phulpur (UP) 5)220/132 kV 160 MVA ICT-2 at Phulpur (UP) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of April 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / los | grid_india_gd/grid_events/2026-04-01
G00213 | 2026-04 | 45 | GD-1 | Bihar | BR | Eastern | 2026-04-20T12:05 | 2026-04-20T13:49 | 1.73 | 0 | 152 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GD-1 Bihar 20-04-2026 12:05 20-04-2026 13:49 01:44 0 152 0.00% 0.52% 23893 29300 Prior to the disturbance 220 kV Raxaul–Sitamarhi Ckt 1 & 2 were under planned shutdown from 11:30 Hrs on 20/04/2026 and Raxaul and Parwanipur areas of Bihar and the Nepal power system were connected to rest of the Eas | 4 GD-1 Bihar 20-04-2026 12:05 20-04-2026 13:49 01:44 0 152 0.00% 0.52% 23893 29300 Prior to the disturbance 220 kV Raxaul–Sitamarhi Ckt 1 & 2 were under planned shutdown from 11:30 Hrs on 20/04/2026 and Raxaul and Parwanipur areas of Bihar and the Nepal power system were connected to rest of the Eastern Region grid through the 220 kV Raxaul–Gopalganj–MTPS double circuit lines. At 12:05 Hrs, 220 kV Gopalganj–MTPS line 1 & 2 tripped due to Y-B phase fault, leading to a power failure at Raxaul and Gopalganj S/s. Total load loss of 152 MW (130 MW at Nepal area) and 22 MW load loss reported at Raxaul Gopalganj S/s. 220 KV-New Raxaul- Gopalganj-1 220 KV-New Raxaul- Gopalganj-2 | grid_india_gd/grid_events/2026-04-01
G00214 | 2026-04 | 34 | GI-1 | Maharashtra | MH | Western | 2026-04-21T00:07 | 2026-04-21T02:17 | 2.17 |  |  | FALSE | TRUE | FALSE | FALSE | TRUE | No generation loss reported at the time of tripping. | 8 GI-1 Maharashtra 21-04-2026 00:07 21-04-2026 02:17 02:10 - - - - 89482 72043 Partial outage of 220 kV Tandulwadi Wind Power Plant(Serentica Renewables):At 00:07 Hrs / 21-04-26, While charging 220/33 kV Tandulwadi ICT 1 through 201 Bay, 220 kV Tandulwadi- Kallam line tripped on line differential protection operation. Due to the loss of evacuation path, 220 kV Tandulwadi Wind Power Plant went dark. No generation loss reported at the time of tripping. 1. 220 kV Tandulwadi - Kallam | grid_india_gd/grid_events/2026-04-01
G00215 | 2026-04 | 19 | GD-1 | Uttar Pradesh | UP | Northern | 2026-04-21T19:29 | 2026-04-22T00:17 | 4.8 | 460 | 100 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, change in demand of approx 100 MW was observed in UP control area and generation loss of approx 460 MW occurred at Harduaganj(UP). | 19 GD-1 Uttar Pradesh 21-04-2026 19:29 22-04-2026 00:17 04:48 460 100 0.75% 0.14% 61422 70083 i)220/132kV Harduaganj (UP) has double main and transfer Bus arrangement at 220kV and single main and transfer Bus arrangement at 132 kV level. ii)During antecedent condition, total Generation of Harduaganj(UP) was approx 460 MW . iii)As reported, at 19:29 hrs, R-ph CT of 220kV Harduaganj(UP)-Khair(UP) Ckt-2 at Harduaganj end got damaged. Fault was sensed in zone-4 at Harduaganj end. iv)During the same time, the circuit breaker of 220 KV Harduaganj(UP) – Khair(UP) Ckt-2 failed to operate. Bus-bar protection was not operational at 220 kV Harduaganj. v)This led to tripping of Unit 8 and other elements connected to 220 kV Main Bus-II, and also Units 7 and 9 connected to Main Bus-I. This led to complete blackout at 220/132kV Harduaganj(UP). vi)As per PMU at Aligarh(PG), R-N phase to earth fault was observed with fault clearance time of 600ms. vii)As per SCADA, change in demand of approx 100 MW was observed in UP control area and generation loss of approx 460 MW occurred at Harduaganj(UP). 1)220 KV Harduaganj(UP) – Khair(UP) Ckt-1 2)220 KV Harduaganj(UP) – Khair(UP) Ckt-2 3)220 KV Harduaganj(UP) – Sikandrarao(UP) Ckt 4)220 KV Harduaganj(UP) – Etah(UP) Ckt 5)220 KV Harduaganj(UP) – Atrauli(UP) Ckt 6)220 KV Harduaganj(UP) – Boner(UP) Ckt 7)220 KV Harduaganj(UP) – Rukhi(UP) Ckt 8)220 KV Harduaganj(UP) Bus Coupler 9)400/220 kV 315 MVA ICT 2 at Harduaganj (UP) 10)110 MW Harduaganj-C TPS - UNIT | grid_india_gd/grid_events/2026-04-01
G00216 | 2026-04 | 35 | GD-1 | Chhattisgarh | CG | Western | 2026-04-23T19:12 | 2026-04-23T20:16 | 1.07 | 640 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Following the loss of the evacuation path, Unit-1 at APL Raipur tripped, resulting in a generation loss of 640 MW. | 9 GD-1 Chhattisgarh 23-04-2026 19:12 23-04-2026 20:16 01:04 640 - 0.72% - 89472 73256 Complete outage of 400 kV APL Raipur:At 19:12 hrs/ 23.04.2026, the 400 kV APL Raipur–Durg D/C line tripped due to an R–E fault. As reported by APL Raipur, the fault was caused by an R-phase pole failure in the 401 bay. Following the loss of the evacuation path, Unit-1 at APL Raipur tripped, resulting in a generation loss of 640 MW. Consequently, the substation was completely black out. 1. 400 kV APL Raipur Durg 1 2 400 kV APL Raipur Durg 2 | grid_india_gd/grid_events/2026-04-01
G00217 | 2026-04 | 46 | GD-1 | Jharkhand | JH | Eastern | 2026-04-24T18:58 | 2026-04-24T19:54 | 0.93 | 0 | 40 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GD-1 Jharkhand 24-04-2026 18:58 24-04-2026 19:54 00:56 0 40 0.00% 0.13% 32411 30942 Prior to the disturbance 220kV Daltonganj-Latehar line kept opened on system requirement. At 18:58 Hrs on 24/04/2026, Y-Earth fault occurred in 220kV Chatra- Latehar line and at the same time 220 kV Daltonganj-Chat | 5 GD-1 Jharkhand 24-04-2026 18:58 24-04-2026 19:54 00:56 0 40 0.00% 0.13% 32411 30942 Prior to the disturbance 220kV Daltonganj-Latehar line kept opened on system requirement. At 18:58 Hrs on 24/04/2026, Y-Earth fault occurred in 220kV Chatra- Latehar line and at the same time 220 kV Daltonganj-Chatra line tripped from Chatra end only, resulting in total power failure at Chatra S/s. Total load loss of around 40 MW reported at Chatra S/s. 220 KV Daltonganj- Chatra 220 kV Latehar- Chatra | grid_india_gd/grid_events/2026-04-01
G00218 | 2026-04 | 20 | GD-1 | Rajasthan | RJ | Northern | 2026-04-25T12:32 | 2026-04-25T17:07 | 4.58 | 21 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vi)As per SCADA, change in solar generation of approx 21 MW was observed at Khidrat(IP). | 20 GD-1 Rajasthan 25-04-2026 12:32 25-04-2026 17:07 04:35 21 0 0.03% 0.00% 67497 65142 i)220kV Khidrat(IP) is connected at Bikaner2(PG) at 220kV level and its generation evacuates through 220 KV Bikaner_2 (PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt. ii)During antecedent condition, 220kV Khidrat(IP) was generating approx 21 MW (as per SCADA). iii)As reported at 12:32 hrs, 220 KV Bikaner_2 (PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt tripped on B-N phase to earth fault (exact reason, nature and location of fault yet to be shared). iv)Due to tripping of this evacuating line, complete blackout occurred at 220kV Khidrat(IP). v)As per PMU at Bikaner2(PG), B-N phase to earth fault was observed with fault clearance time of 80ms. vi)As per SCADA, change in solar generation of approx 21 MW was observed at Khidrat(IP). 1)220 KV Bikaner_2 (PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt | grid_india_gd/grid_events/2026-04-01
G00219 | 2026-04 | 36 | GI-1 | Gujarat | GJ | Western | 2026-04-25T12:45 | 2026-04-25T18:40 | 5.92 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-1 Gujarat 25-04-2026 12:45 25-04-2026 18:40 05:55 - - - - 89482 73636 Complete outage of 220kV Ratadiya(Adani): At 12:45 hrs/25.04.2026, B-phase to earth fault occurred on the bhuj–ratadiya circuit-1 due to a tree came in contact with conductor, resulting in line tripping. No load loss occurre | 10 GI-1 Gujarat 25-04-2026 12:45 25-04-2026 18:40 05:55 - - - - 89482 73636 Complete outage of 220kV Ratadiya(Adani): At 12:45 hrs/25.04.2026, B-phase to earth fault occurred on the bhuj–ratadiya circuit-1 due to a tree came in contact with conductor, resulting in line tripping. No load loss occurred, as the load was transferred to an alternate line. 1.220kV Ratadiya - Bhuj 1 | grid_india_gd/grid_events/2026-04-01
G00220 | 2026-04 | 21 | GD-1 | Rajasthan | RJ | Northern | 2026-04-25T20:19 | 2026-04-25T21:40 | 1.35 | 0 | 250 | FALSE | FALSE | FALSE | FALSE | FALSE | 21 GD-1 Rajasthan 25-04-2026 20:19 25-04-2026 21:40 01:21 0 250 0.00% 0.35% 60703 70604 i)220/132kV Sawaimadhopur(RS) has double main and transfer bus scheme at both 220kV and 132kV level. ii)During antecedent condition, 220/132kV 160 MVA ICT-1 and 100 MVA ICT-2 at Sawaimadhopur(RS) were carrying ap | 21 GD-1 Rajasthan 25-04-2026 20:19 25-04-2026 21:40 01:21 0 250 0.00% 0.35% 60703 70604 i)220/132kV Sawaimadhopur(RS) has double main and transfer bus scheme at both 220kV and 132kV level. ii)During antecedent condition, 220/132kV 160 MVA ICT-1 and 100 MVA ICT-2 at Sawaimadhopur(RS) were carrying approx 103 MW and 91 MW (as per SCADA). iii)As reported, at 20:19 hrs, B-ph CT of 220 KV Anta(NT)-Sawaimadhopur(RS) (PG) Ckt got damaged at Sawaimadhopur(RS) end creating B-N phase to earth fault with fault distance of 104km from Anta end. iv)As per DR of 220 KV Anta(NT)-Sawaimadhopur(RS) (PG) Ckt, fault current was ~3.85kA from Sawaimadhopur(RS) end; fault sensed in zone-1 at Swaimadhopur(RS) end. After approx 280 ms, another B-N phase to earth fault sensed in zone-4 at Swaimadhopur(RS) end. v)As per DR of 220 KV Sawaimadhopur(RS) -Dausa(RS) (PG) Ckt, fault current was ~1.76kA from Sawaimadhopur(RS) end; fault sensed in zone-4 at Swaimadhopur(RS) end and line tripped from Sawaimadhopur(RS) end only. vi)During the same time, bus bar protection operated at 220kV Bus-2 at Sawaimadhpur(RS) (exact reason of busbar protection operation yet to be shared). Due to this, complete blackout occurred at 220/132kV Sawaimadhopur(RS). vii)As per PMU at Dausa(PG), B-N phase to earth fault was observed with fault clearing time of 120 ms . viii)As per SCADA, change in demand of approx 250 MW was observed in Rajasthan control area. 1)220 KV Sawaimadhopur(RS)-Dausa(RS) (PG) Ckt 2)220 KV Anta(NT)-Sawaima | grid_india_gd/grid_events/2026-04-01
G00221 | 2026-04 | 47 | GD-1 | West Bengal | WB | Eastern | 2026-04-26T00:09 | 2026-04-26T00:32 | 0.38 | 0 | 80 | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GD-1 West Bengal 26-04-2026 00:09 26-04-2026 00:32 00:23 0 80 0.00% 0.25% 35069 32034 Prior to the disturbance 220kV bus coupler at Dalkhola(PG) was in off condition due to system requirement and Dalkhola(WB) was radially connected through 220kV Kishanganj-Dalkhola(PG)-Dalkhola(WB) D/C line. At 00 | 6 GD-1 West Bengal 26-04-2026 00:09 26-04-2026 00:32 00:23 0 80 0.00% 0.25% 35069 32034 Prior to the disturbance 220kV bus coupler at Dalkhola(PG) was in off condition due to system requirement and Dalkhola(WB) was radially connected through 220kV Kishanganj-Dalkhola(PG)-Dalkhola(WB) D/C line. At 00:09 Hrs on 26/04/2026, 220kV Kishanganj-Siliguri-1 and 220 kV Kishanganj- Dalkhola(PG) D/C tripped due to inclement weather on B-Earth fault. This resulted in 220 kV bus dead at Dalkhola(WB). Total load loss of 80 MW reported at Dalkhola(WB). 220KV-KISHANGANJ(PG)-DALKHOLA (PG)-1 220KV-KISHANGANJ(PG)-DALKHOLA (PG)-2 220KV-SILIGURI-KISHANGANJ(PG)-1 | grid_india_gd/grid_events/2026-04-01
G00222 | 2026-04 | 22 | GD-1 | Rajasthan | RJ | Northern | 2026-04-26T14:49 | 2026-04-26T15:04 | 0.25 | 278 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of approx 68 MW occurred at VSLPP(RS). | 22 GD-1 Rajasthan 26-04-2026 14:49 26-04-2026 15:04 00:15 278 0 0.45% 0.00% 61920 62067 i)220/132kV Bikaner(RS) has double main and transfer bus scheme and 220kV VSLPP(RS) has double main bus scheme at 220kV level. ii)During antecedent condition, 135 MW VSLPP (IPP) - UNIT 1 was generating approx 68 MW (as per SCADA). iii)As reported, at 14:48 hrs, 220 KV Bikaner(RS)-Bikaner400(RS) Ckt-3 tripped from Bikaner400(RS) end only on R-Y phase to phase fault with fault distance of 2.984km from Bikaner400(RS) end; zone-1 distance protection operated at Bikaner400(RS) end. iv)Further, as reported, at 14:49 hrs, 220 KV Bikaner(RS)-Bikaner400(RS) Ckt-1 tripped from Bikaner220(RS) end only on R-Y-B 3 phase fault with fault distance of 3.33km from Bikaner220(RS) end; zone-1 distance protection operated at Bikaner220(RS) end. v)During this fault, all other 220kV lines connected at Bikaner(RS) tripped from remote ends only on zone-3 distance protection operation. Due to this, complete blackout occurred at 220/132kV Bikaner(RS). vi)Further, due to tripping of 220 KV Bikaner(RS)-VSLPP Ckt (only available evacuating line), 135 MW VSLPP (IPP) - UNIT 1 also tripped due to loss of evacuation path and complete blackout occurred at 220kV VSLPP(RS). vii)As per PMU at Bikaner(IP), Y-N phase to earth fault followed by R-N phase to earth fault was observed with fault clearing time of 80 ms each; however voltage dip observed in all 3-phases in both the cases. viii)As per SCADA, change in Solar generation | grid_india_gd/grid_events/2026-04-01
G00223 | 2026-04 | 23 | GD-1 | Haryana | HR | Northern | 2026-04-27T06:33 | 2026-04-27T11:16 | 4.72 | 396 | 300 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 396 MW occurred at Panipat TPS. | 23 GD-1 Haryana 27-04-2026 06:33 27-04-2026 11:16 04:43 396 300 0.74% 0.46% 53626 64547 i)220/132kV Bastra(HR) has double main bus scheme at 220kV level. ii)During antecedent condition, 250 MW Panipat TPS - UNIT 7 & 8 were generating approx 204 MW and 192 MW respectively. iii)As reported, at 06:33 hrs, R and Y-ph CTs of 220kV Bastra-Safidon (HR) Ckt and B-ph CT of 220kV Panipat TPS-Bastra (HR) Ckt got damaged at Bastra end and all 220kV lines connected at Bastra(HR) tripped (exact reason, nature and location of fault and nature of protection operation yet to be shared). Due to this, complete blackout occurred at 220/132kV Bastra(HR). iv)During the same time, 220kV Panipat TPS-Safidon (HR) Ckt-1, 2 & 3 and 250 MW Panipat TPS - UNIT 7 & 8 also tripped (exact reason and nature of protection operation yet to be shared). v)As per PMU at Panipat(BB), 3 Phase to earth fault with delayed fault clearing time of 400 ms was observed. vi)As per SCADA change in demand of approx 300 MW in Haryana control area was observed. Generation loss of approx 396 MW occurred at Panipat TPS. 1)220kV Panipat TPS-Bastra (HR) Ckt 2)220kV Panipat TPS-Safidon (HR) Ckt-1 3)220kV Panipat TPS-Safidon (HR) Ckt-2. 4)220kV Panipat TPS-Safidon (HR) Ckt-3 5)250 MW Panipat TPS - UNIT 7 6)250 MW Panipat TPS - UNIT 8 7)220kV Bastra-Kaul1 (HR) Ckt 8)220kV Bastra-Kurukshetra HVDC Ckt 9)220kV Bastra-Safidon (HR) Ckt | grid_india_gd/grid_events/2026-04-01
G00224 | 2026-04 | 37 | GD-1 | Maharashtra | MH | Western | 2026-04-28T02:53 | 2026-04-28T11:54 | 9.02 | 5 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 5 MW occurred at 220 kV Tandulwadi Wind Power Plant due to loss of evacuation path. | 11 GD-1 Maharashtra 28-04-2026 02:53 28-04-2026 11:54 09:01 5 - 0.01% - 86554 69763 Complete outage of 220 kV Tandulwadi Wind Power Plant(Serentica Renewables): At 02:53 hrs/28.04.2026, during charging of 220/33 kV Tandulwadi ICT-2, the 220 kV Tandulwadi–Kallam transmission line tripped due to the operation of line differential protection. Generation loss of 5 MW occurred at 220 kV Tandulwadi Wind Power Plant due to loss of evacuation path. 1. 220 kV Tandulwadi - Kallam | grid_india_gd/grid_events/2026-04-01
G00225 | 2026-04 | 39 | GD-1 | Gujarat | GJ | Western | 2026-04-28T14:05 | 2026-04-28T22:30 | 8.42 | 107 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 107 MW occurred at 220 kV Jhura Renewable Energy (RE) station due to loss of the evacuation path. | 13 GD-1 Gujarat 28-04-2026 14:05 28-04-2026 22:30 08:25 107 - 0.11% - 93196 74347 Complete outage of 220kV Jhura Wind RE Plant (Ayana Power):At 14:05 hrs/ 28-04-2026, the 220 kV Bhuj–Jhura transmission line tripped due to a B-phase to ground fault. Generation loss of 107 MW occurred at 220 kV Jhura Renewable Energy (RE) station due to loss of the evacuation path. 1. 220kV Bhuj Jhura S/C 14 Not an event Maharashtra 02-04-2026 00:28 02-04-2026 04:09 03:41 - - - - 73672 62990 765/400kV Wardha PG: At 00.28.52 Hrs./02.04.2026, feeders mentioned below were tripped at Wardha Substation due to internal flashover of 765kV oil filled porcelain CTs of Arteche Make in bay no. 717, 711 and 715 during inclement weather. 1. Wardha - 765KV - Bus 2 2. Wardha - 765KV B/R 2 3. 765KV-Wardha-Aurangabad-1 4. 765KV-Seoni-Wardha-1 5. 765KV-Wardha-Raipur-PS (Durg)-3 6. 765KV-Wardha-Raipur-PS (Durg)-4 7. Wardha - 765KV B/R 3 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 KARNATAKA 05-04-2026 08:55 05-04-2026 10:13 01:18 10 0 0.02% 0.00% 48567.68 59453.82 Complete outage of 220kV RSRPL_GadagPS of RENEW As per the reports submitted, the triggering incident was YB-G fault in 220kV Gadag RSRPL_Gadag_PS line at 205 line bay at RSRPL end. At RSRPL end, the fault was sensed in I>4 non directional over current protection and 3ph tripped. However the line tripped only at RSRP | grid_india_gd/grid_events/2026-04-01
G00226 | 2026-04 | 38 | GI-1 | Maharashtra | MH | Western | 2026-04-28T20:55 | 2026-04-30T15:41 | 42.77 |  |  | FALSE | TRUE | FALSE | FALSE | TRUE | 12 GI-1 Maharashtra 28-04-2026 20:55 30-04-2026 15:41 42:46 - - - - 89806 72200 Partial outage of 220 kV Tandulwadi Wind Power Plant(Serentica Renewables):At 20:55 hrs/28.04.2026, during charging of 220/33 kV Tandulwadi ICT-02, ICT-02 tripped due to the operation of Busbar protection. | 12 GI-1 Maharashtra 28-04-2026 20:55 30-04-2026 15:41 42:46 - - - - 89806 72200 Partial outage of 220 kV Tandulwadi Wind Power Plant(Serentica Renewables):At 20:55 hrs/28.04.2026, during charging of 220/33 kV Tandulwadi ICT-02, ICT-02 tripped due to the operation of Busbar protection. 1. 220 kV Tandulwadi - Kallam | grid_india_gd/grid_events/2026-04-01
G00227 | 2026-04 | 24 | GD-1 | Uttar Pradesh | UP | Northern | 2026-04-29T16:15 | 2026-04-29T17:32 | 1.28 | 0 | 50 | FALSE | FALSE | FALSE | FALSE | FALSE | 1)400 KV Varanasi(PG)-Sahupuri(UP) (PG) Ckt-1 2)220 KV Bhelupur-Sahupuri(UP) Ckt 3)400 KV Varanasi(PG)-Sahupuri(UP) (PG) Ckt-2 4)400 KV Sahupuri(UP)-Biharshariff(PG) (PG) Ckt-2 5)400 KV Sahupuri(UP)-Biharshariff(PG) (PG) Ckt-1 6)220KV Sahupuri220- Sahupuri(UP) Ckt-1 7)220KV Sahupuri220- Sahupuri(UP) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Gene | 24 GD-1 Uttar Pradesh 29-04-2026 16:15 29-04-2026 17:32 01:17 0 50 0.00% 0.08% 60491 64547 i)400/220kV Sahupuri(UP) has double main Bus arrangement at both 400kV and 220kV level. ii)As reported, during 16:03 hrs-16:15 hrs, all 400kV and 220kV lines connected from 400/220kV Sahupuri(UP) tripped on multiple faults due to heavy rain and storm accompanied by gusty winds gusting to 70kmph at isolated places. Due to this, at 16:15 hrs, complete blackout occurred at 400/220kV Sahupuri(UP) S/s. iii)Sequence of the event as per DR, PMU and SCADA SOE is as follows: At 16:03 hrs: First a transient B-N phase to earth fault (Ib=~860A from Sahupuri) appeared on 400 KV Varanasi(PG)-Sahupuri(UP) (PG) Ckt-1 and A/R successfully operated from both the ends. However after ~5s, Y-B-N double phase to earth fault (fault distance: 1.876km and Iy=~10.596kA, Ib=~10.192kA from Sahupuri) occurred on 400 KV Varanasi(PG)-Sahupuri(UP) (PG) Ckt-1 and zone-1 distance protection operated at Sahupuri end and the line tripped. At 16:06 hrs: 220 KV Bhelupur-Sahupuri(UP) Ckt tripped on Y-B phase to phase fault as per PMU (exact nature and location of fault & DR yet to be shared). At 16:07 hrs: First a transient B-N phase to earth fault (Ib=~5.493kA from Sahupuri) appeared on 400 KV Varanasi(PG)-Sahupuri(UP) (PG) Ckt-2 and A/R successfully operated from both the ends. However after ~5s, Y-N phase to earth fault (fault distance: 2.314km and Iy=~5.405kA, from Sahupuri) occurred within reclaim time on 400 KV Varanas | grid_india_gd/grid_events/2026-04-01
G00228 | 2026-04 | 25 | GI-2 | Uttar Pradesh | UP | Northern | 2026-04-30T06:28 | 2026-04-30T09:44 | 3.27 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 25 GI-2 Uttar Pradesh 30-04-2026 06:28 30-04-2026 09:44 03:16 0 0 0.00% 0.00% 48617 58319 i)765/400kV Agra(PG) have one and half breaker bus scheme at both 765 & 400kV level. ii)During antecedent condition, 765 KV Agra-Gwalior (PG) ckt-1 & 2 were carrying ~47 MW each. As reported, there was inclemen | 25 GI-2 Uttar Pradesh 30-04-2026 06:28 30-04-2026 09:44 03:16 0 0 0.00% 0.00% 48617 58319 i)765/400kV Agra(PG) have one and half breaker bus scheme at both 765 & 400kV level. ii)During antecedent condition, 765 KV Agra-Gwalior (PG) ckt-1 & 2 were carrying ~47 MW each. As reported, there was inclement weather condition (thunderstorm / lightning). iii)As reported, at 06:28 hrs, 765 KV Agra-Jhatikara (PG) Ckt-1, 765 KV Agra-Fatehpur (PG) Ckt-1, 765 KV Agra-Gwalior (PG) Ckt-1 & 2, 765/400 kV 1500 MVA ICT 1 at Agra(PG) and 240 MVAR Bus Reactor No 1 & 2 at 765KV Agra(PG) tripped. Tripping occurred due to phase to earth faults in lines due to thunderstorm / lightning during inclement weather conditions. iv)As per PMU plot of phase voltage and currents of all the tripped lines at Agra(PG), it was observed that at first instance i.e., 06:28 29 hrs, B-N fault occurred on 765 KV Agra-Jhatikara (PG) Ckt-1. On this fault line successfully autoreclosed however tripped on B-N fault in reclaim time. Further, at 06:28:34hrs, 765 KV Agra-Fatehpur (PG) Ckt-1 tripped on R-N fault without A/R operation. Further at 06:28:41 hrs, 765 KV Agra-Gwalior (PG) Ckt-1 tripped on R-N fault without A/R operation. Further at 06:28:40 hrs, 765 KV Agra-Gwalior (PG) Ckt-2 tripped on R-N fault in reclaim time after successful A/R operation. 240 MVAr bus reactor-1 & 2 also tripped along with the 765 KV Agra-Gwalior (PG) Ckt-1 & 765 KV Agra-Jhatikara (PG) Ckt-1 respectively (bus reactor and both the lines were on t | grid_india_gd/grid_events/2026-04-01
G00229 | 2026-04 | 41 | GI-1 | Andhra Pradesh | AP | Southern | 2026-04-30T13:16 | 2026-04-30T13:29 | 0.22 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 13 GI-1 ANDHRA PRADESH 30-04-2026 13:16 30-04-2026 13:29 00:13 0 0 0.0 % 0.0 % 55224.66 65542.6 Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO The triggering incident is the B-G fault in 220KV-CHILLAKALLU-PULICHINTALA-1, during which B-ph breaker failed to open at CHILLAKALLU end and led to the LBB operation in Bus-2 and all elements connected to Bus-2 at CHILLAKALLU tripped and led to the Tripping of 220kV Bus-2 of Chilakallu of APTRANSCO 220KV-KONDAPALLI-CHILLAKALLU-2, 220KV-VTPS-CHILLAKALLU-2, CHILLAKALLU - 220KV - Bus 2 Details of Grid Events during the Month of April 2026 in Southern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-04-01
G00230 | 2026-04 | 26 | GI-2 | Haryana | HR | Northern | 2026-04-30T18:36 | 2026-04-30T20:19 | 1.72 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 26 GI-2 Haryana 30-04-2026 18:36 30-04-2026 20:19 01:43 0 0 0.00% 0.00% 49088 56303 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total 1000 MW power from Champa to Kurukshetra (250 MW on each Pole as per SCADA). ii)As reported, at 18:36 hrs, 800 KV HVDC Kurukshetra(PG) Pole-2 tripped on DC line fault due to jumper swing at Tower location no. 2482. iii)During the same time, 800 KV HVDC Kurukshetra (PG) pole 4 also tripped (exact reason of tripping and nature of protection operated yet to be shared). iv)As per PMU at Kurukshetra (PG), no fault was observed in the system. v)As per SCADA, no change in demand in Haryana control area and no change in power order was observed. The power order of Pole-1 & 3 ramped up to compensate the Power of Pole 2 & 4. vi)As remedial action taken, insulation tape was applied on tower legs and step bolts were opened which are in reach of jumper swing. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-04-01
G00231 | 2026-04 | 48 | GD-1 | Bihar | BR | Eastern | 2026-04-30T19:05 | 2026-04-30T19:30 | 0.42 | 0 | 113 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GD-1 Bihar 30-04-2026 19:05 30-04-2026 19:30 00:25 0 113 0.00% 0.58% 32226 19569 Prior to the disturbance 220kV Muzaffarpur-Goraul-1 line tripped at 18:57 Hrs on 30/04/2026 and 220kV Goraul S/s radially connected to 220kV Muzaffarpur S/s through 220kV Muzaffarpur-Goraul-2 line. At 19:06 Hrs on 30/04/2026, 220kV Muzaffarpur-Goraul-2 line tripped on B-Earth fault, resulted in 220kV Goraul S/s became dead. Total load loss of 113 MW reported at Goraul S/s. 220kV Muzaffarpur-Goraul Ckt#2 Elements Tripped Details of Grid Events during the Month of April 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD I Manipur 02-04-2026 03:05 02-04-2026 03:58 00:53 0 1 0.00% 0.07% 2486 1463 Rengpang area of Manipur Power System was connected with rest of NER Grid through 132kV Loktak Rengpang line. The 132kV-Jiribam-Rengpang line was under long outage since 18:18 Hrs of 17.11.2023. At 03:05 Hrs of 02-04-2026, 132kV Loktak - Rengpang line tripped. Due to | grid_india_gd/grid_events/2026-04-01
G00232 | 2026-05 | 47 | GD-1 | Gujarat | GJ | Western | 2026-05-01T12:55 | 2026-05-01T13:56 | 1.02 | 390 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 390 MW Occurred at Ratadiya (Adani) due to loss of evacuation path. | 1 GD-1 Gujarat 01-05-2026 12:55 01-05-2026 13:56 01:01 390 - 0.51% - 76136 64472 Complete outage of 220 kV Ratadiya (Adani): At 12:55 hrs / 01-05-2026, 220 kV Bhuj-Ratadiya-1 tripped on B-E Fault, auto recloser unsuccessful at both ends. Following Circuit‑1 tripping, the parallel 220 kV Bhuj–Ratadiya-2 got overloaded and tripped. As per the field intimation, the physical root cause was identified at Suspension Tower No. 99, where the suspension insulator/hardware failed (insulator hook detached from cross-arm leading to flashover and insulator puncture/detachment).The Special Protection Scheme at 220 kV Ratadiya Pooling Station didn’t operate (Special Protection Scheme is specifically designed to prevent tripping of the healthy 220 kV Bhuj–Ratadiya circuit due to post- contingency overloading when the other circuit is open). Generation loss of 390 MW Occurred at Ratadiya (Adani) due to loss of evacuation path. 1. 220 kV Bhuj-Ratadiya-1 2. 220 kV Bhuj-Ratadiya-2 | grid_india_gd/grid_events/2026-05-01
G00233 | 2026-05 | 48 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-01T17:12 | 2026-05-01T19:14 | 2.03 | 530 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of both the line the unit got tripped due to loss of evacuation path and 400 kV Jhabua S/S got dead with generation loss of 530 MW. | 2 GD-1 Madhya Pradesh 01-05-2026 17:12 01-05-2026 19:14 02:02 530 - 0.65% - 81413 66192 Complete outage of 400 kV Jhabua Power: At 17:18:06 Hrs/ 01.05.2026, 400 kV Jhabua Jabaplpur-1 line tripped on B-N fault. Prior to the event, at 17:12:03:163- 400 kV Jhabua Jabaplpur-2 line tripped on B-N fault in reclaim time 2 seconds after successful A/R on R-N fault. Due to tripping of both the line the unit got tripped due to loss of evacuation path and 400 kV Jhabua S/S got dead with generation loss of 530 MW. One transmission tower (Tower No-183) was found to be damaged and in tilted condition during patrolling. Ckt-2 was charged after isolating Ckt-1. 1 400kV Jhabua Jabalpur -1 2 400 kV Jhabua Jabalpur -2 | grid_india_gd/grid_events/2026-05-01
G00234 | 2026-05 | 73 | GD-1 | Jharkhand | JH | Eastern | 2026-05-01T22:33 | 2026-05-01T23:47 | 1.23 | 0 | 248 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 Jharkhand 01-05-2026 22:33 01-05-2026 23:47 01:14 0 248 0.00% 1.08% 33976 22898 220kV Godda S/s and Jasidih S/s connected with 220kV Dumka S/s via 220kV D/C line. At 22:33 Hrs on 01/05/2026, R-Eath fault occurred in 220kV Dumka-Godda-1 line and Z-1 protection operated from both ends. Line tri | 1 GD-1 Jharkhand 01-05-2026 22:33 01-05-2026 23:47 01:14 0 248 0.00% 1.08% 33976 22898 220kV Godda S/s and Jasidih S/s connected with 220kV Dumka S/s via 220kV D/C line. At 22:33 Hrs on 01/05/2026, R-Eath fault occurred in 220kV Dumka-Godda-1 line and Z-1 protection operated from both ends. Line tripped from Godda end but R-phase CB didn’t open from Dumka end resulting Z-3 protection operation from remote end for all emanating lines from Dumka S/s. 220kV Dumka S/s, Godda and Jasidih S/s became dead. Total load loss of 248 MW reported at Dumka, Godda and Jasidih S/s. 220 KV Maithon- Dumka-1 220 KV Maithon- Dumka-2 220 KV Godda- Dumka-1 220 KV Godda- Dumka-2 220 KV Govindpur- Dumka-1 220 KV Govindpur- Dumka-2 | grid_india_gd/grid_events/2026-05-01
G00235 | 2026-05 | 3 | GD-1 | Uttarakhand | UK | Northern | 2026-05-02T05:03 | 2026-05-02T05:39 | 0.6 | 122 | 64 | FALSE | FALSE | FALSE | FALSE | FALSE | As reported, load loss of 64 MW occurred at Majri(HP) and generation loss of 80 MW at Chhibro and 42 MW at Khodri occurred. | 3 GD-1 Uttarakhand 02-05-2026 05:03 02-05-2026 05:39 00:36 122 64 28.39% 11.08% 42968 57736 i)220KV Khodri(UK) generating station have 4 generating units each of 30MW and 220kV Chhibro(UK) generating station have 4 generating units each of 60MW and both generating station have double main bus scheme. ii)During antecedent condition, Unit-2 & Unit-3 of Khodri(UK) and Unit-2 & Unit-4 of Chhibro (UK) were in running condition and was generating approx 22 MW , 21 MW , 44MW, 51MW respectively (as per SCADA). iii)As reported, at 05:03 hrs, a fault occurred in 220 KV Saharanpur(UP)-Khodri(UK) (UP) Ckt which was sensed in zone-2 at Khodri end (exact reason, nature and location of fault yet to be shared). iv)On this fault, standby earth fault (51N) initiated on generator protection relays of 30 MW Unit-2 & 3 at Khodri(UK) and eventually LBB protection operated in both the units (reason of LBB operation yet to be shared). v)On this, complete blackout occurred at 220kV Khodri(UK) and 220kV Chhibro(UK). vi)As per PMU at Saharanpur(PG), B-N phase to earth fault with fault clearing time of 80 ms was observed. vii)As per SCADA, change in geneartion of approx 125 MW was observed in UƩarakhand control area. As reported, load loss of 64 MW occurred at Majri(HP) and generation loss of 80 MW at Chhibro and 42 MW at Khodri occurred. 1) 220 KV Khodri(UK)-Majri(HP) (UK) Ckt-1 2) 220 KV Khodri(UK)-Majri(HP) (UK) Ckt-2 3) 220 KV Khodri - Chhibro (UK) Ckt-1 4) 220 KV Khodri - Chhibro (UK) Ckt-2 5) 220 | grid_india_gd/grid_events/2026-05-01
G00236 | 2026-05 | 50 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-02T15:23 | 2026-05-02T16:10 | 0.78 | 85 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 85 MW Occurred at Shajapur (NTPC) due to loss of evacuation path. | 4 GD-1 Madhya Pradesh 02-05-2026 15:23 02-05-2026 16:10 00:47 85 - 0.10% - 89040 71516 Complete outage of 220 kV Shajapur Unit-06 and 220 kV Shajapur Unit-07 (NTPC): At 15:23 hrs / 02-05-2026, 220 kV Shajapur Unit06-Shajapur Unit07-1 S/C tripped on differential protection operated (as reported by NTPC). As intimated by site, no abnormality was found during patrolling and line was successfully charged in 47 minutes. Generation loss of 85 MW Occurred at Shajapur (NTPC) due to loss of evacuation path. 1. 220 kV Shajapur Unit06-Shajapur Unit07-1 S/C | grid_india_gd/grid_events/2026-05-01
G00237 | 2026-05 | 1 | GI-2 | Haryana | HR | Northern | 2026-05-02T16:31 | 2026-05-02T18:47 | 2.27 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-2 Haryana 02-05-2026 16:31 02-05-2026 18:47 02:16 0 0 0.00% 0.00% 50314 65085 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole (as per SCADA). At 10:24 AM, the Backup Telecom Link Fail alarm got latch | 1 GI-2 Haryana 02-05-2026 16:31 02-05-2026 18:47 02:16 0 0 0.00% 0.00% 50314 65085 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole (as per SCADA). At 10:24 AM, the Backup Telecom Link Fail alarm got latched. From this time onward, multiple power imbalance events were observed between Pole‑2 and Pole‑4, indicating instability in HVDC control and communication. Due to the backup telecom link issue, P2P communication of Pole‑1 and Pole‑3 started toggling intermittently. Consequently, the other‑end current value remained latched to a previous value, leading to improper current feedback. ii)As reported, at 16:31 hrs, 800 KV HVDC Kurukshetra(PG) Pole-1 & 3 got blocked from Champa on CLD HV protection, as the controller detected abnormal conditions based on incorrect current feedbacktripped due to CLD operated at Champa end. iii)After the blocking of Pole‑1 and Pole‑3, the remaining healthy poles (Pole‑2 and Pole‑4) were expected to automatically compensate for the lost power, as per normal HVDC control philosophy. However, this compensation did not occur correctly. Instead, severe power imbalance was observed: Pole‑2 power reduced to ~80 MW against a scheduled value of 750 MW and Pole‑4 power increased to ~1800 MW against its scheduled value of 750 MW. iv)As per PMU at Kurukshetra (PG), no fault was observed in the system, however fluctuation in voltage was observed in both the instances | grid_india_gd/grid_events/2026-05-01
G00238 | 2026-05 | 49 | GI-2 | Madhya Pradesh | MP | Western | 2026-05-02T16:45 | 2026-05-02T18:12 | 1.45 | 152 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of Satpura Unit- 11, generation loss of 152 MW was observed at 400 kV Satpura S/S. | 3 GI-2 Madhya Pradesh 02-05-2026 16:45 02-05-2026 18:12 01:27 152 - 0.17% - 89865 68881 Partially outage of 400 kV Satpura: At 16:45 hrs on 02.05.2026, 400 kV Satpura Bus-I tripped due to operation of the Busbar Protection Scheme, resulting in tripping of all connected elements including Satpura–Seoni, Satpura–Itarsi, Satpura–Astha-I lines, Satpura Unit-11, Bus Reactor and Bus Coupler. The disturbance occurred during severe storm conditions when a tree branch from outside the switchyard boundary came in close proximity to the Y-phase of 400 kV Main Bus-I, causing a busbar fault. Due to tripping of Satpura Unit- 11, generation loss of 152 MW was observed at 400 kV Satpura S/S. 1. 400 kV Satpura Bus 1 2. 400 kV Satpura- Seoni 3. 400 kV Satpura- Itarsi 4. 400 kV Satpura- Astha 1 5. Satpura Unit 11 (250 MW) 6. 400kV 50MVA Station Transformer-11 7. 400 kV Satpura Bus Reactor-1 | grid_india_gd/grid_events/2026-05-01
G00239 | 2026-05 | 2 | GI-2 | Haryana | HR | Northern | 2026-05-02T16:51 | 2026-05-02T19:18 | 2.45 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GI-2 Haryana 02-05-2026 16:51 02-05-2026 19:18 02:27 0 0 0.00% 0.00% 48132 64977 i)Due to this excessive loading, at 16:51 hrs, 800 KV HVDC Kurukshetra(PG) Pole- 4 exceeded its overcurrent limit, which resulted in DC Overcurrent Protection operation, and consequently Pole‑4 got blocked and generat | 2 GI-2 Haryana 02-05-2026 16:51 02-05-2026 19:18 02:27 0 0 0.00% 0.00% 48132 64977 i)Due to this excessive loading, at 16:51 hrs, 800 KV HVDC Kurukshetra(PG) Pole- 4 exceeded its overcurrent limit, which resulted in DC Overcurrent Protection operation, and consequently Pole‑4 got blocked and generates CAT-B which resulted in blocking of 800 KV HVDC Kurukshetra(PG) Pole-2. ii)As per PMU at Kurukshetra (PG), no fault was observed in the system, however fluctuation in voltage was observed in both the instances. iii)As per SCADA, no change in demand in Haryana control area was observed. Change in power order of approx 1770 MW was observed. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 | grid_india_gd/grid_events/2026-05-01
G00240 | 2026-05 | 51 | GD-1 | Maharashtra | MH | Western | 2026-05-02T19:14 | 2026-05-02T23:17 | 4.05 | 242 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 242 MW occurred due to the tripping of IEPL Unit 1 (270 MW). | 5 GD-1 Maharashtra 02-05-2026 19:14 02-05-2026 23:17 04:03 242 - 0.30% - 81655 66435 Complete outage of 400 kV IEPL Thermal Power Plant: At 19:14 Hrs/02-05-2026, 400kV IEPL Warora & 400 kV IEPL-Koradi lines tripped on B-E fault. Inadvertent trippings were observed at IEPL end. Due to the loss of evacuation path, 400kV IEPL Thermal Power Plant went into dark. Generation loss of 242 MW occurred due to the tripping of IEPL Unit 1 (270 MW). 1. 400 kV IEPL Koradi 2. 400 kV IEPL Warora-2 3. IEPL Unit 1 (270 MW) | grid_india_gd/grid_events/2026-05-01
G00241 | 2026-05 | 4 | GD-1 | Haryana | HR | Northern | 2026-05-03T21:16 | 2026-05-04T02:22 | 5.1 | 0 | 53 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GD-1 Haryana 03-05-2026 21:16 04-05-2026 02:22 05:06 0 53 0.00% 8.06% 49769 65722 i)220/132kV Isherwal(HR) has double main bus scheme at both 220kV level 132kV level. ii)During antecedent condition, 220kV Isherwal-Sagwan Ckt-1 & 2 were out of service and 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ck | 4 GD-1 Haryana 03-05-2026 21:16 04-05-2026 02:22 05:06 0 53 0.00% 8.06% 49769 65722 i)220/132kV Isherwal(HR) has double main bus scheme at both 220kV level 132kV level. ii)During antecedent condition, 220kV Isherwal-Sagwan Ckt-1 & 2 were out of service and 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 & 2 were carrying approx 20 MW each (as per SCADA). iii)As reported, at 21:16 hrs, 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 & 2 tripped on B-N phase to earth fault(exact reason, nature and location of fault yet to be shared). iv)Due to tripping of both 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 & 2, complete blackout occurred at 220/132kV Isherwal(HR) S/s. v)As per PMU at Bhiwani(PG), two consecutive B-N phase to earth faults were observed with fault clearing time of 80 ms and 400 ms (delayed) respectively. vi)As per SCADA, change in demand of approx 53 MW was observed at Haryana Control area. 1) 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 2) 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-2 | grid_india_gd/grid_events/2026-05-01
G00242 | 2026-05 | 5 | GD-1 | Uttarakhand | UK | Northern | 2026-05-04T08:41 | 2026-05-04T09:52 | 1.18 | 0 | 110 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GD-1 Uttarakhand 04-05-2026 08:41 04-05-2026 09:52 01:11 0 110 0.00% 24.82% 49491 44324 i)Power of 33*3MW Singoli Bhatwari HEP evacuates through 220 KV Singoli Bhatwari (Singoli(LTUHP)) (end)-Srinagar(UK) (PTCUL) Ckt-1 & 2. ii)During antecedent condition, 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK | 5 GD-1 Uttarakhand 04-05-2026 08:41 04-05-2026 09:52 01:11 0 110 0.00% 24.82% 49491 44324 i)Power of 33*3MW Singoli Bhatwari HEP evacuates through 220 KV Singoli Bhatwari (Singoli(LTUHP)) (end)-Srinagar(UK) (PTCUL) Ckt-1 & 2. ii)During antecedent condition, 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK) Ckt-2 was not in service and there was no generation at 220 KV Singoli Bhatwari. iii)As reported, at 08:40 hrs, CT punctured at Alaknanda end of 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt and line tripped on 3 phase to earth fault (exact nature and location of fault yet to be shared). iv)Further, at 08:41 hrs, 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK) Ckt-1 tripped on R-N phase to earth fault with fault location of 2.01km from Srinagar(UK) end after unsuccessful A/R attempt. v)Due to supply fail, 220 KV Singoli Bhatwari(Singoli(LTUHP))-Srinagar(UK) (PTCUL) Ckt-1 & 2 also opened by Singoli end and DT received at Srinagar end. vi)Due to this event, complete blackout occurred at 220kV Singoli Bhatwari HEP(Singoli(LTUHP)) and 400/220/132kV Srinagar(UK) S/s. vii)As per PMU at Rishikesh(UK), 3 phase to earth fault followed by R-N phase to earth fault with unsuccessful A/R with fault clearance time of 160 ms, 120 ms & 80 ms respectively was observed. viii)As per SCADA, change in demand of approx 110 MW in UƩarakhand control area was observed. 1) 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt 2) 400 KV Alaknanda GVK(UPC)-Srinagar(UK) (UK) Ckt-1 3) 220 KV Singoli Bhatwari (Singo | grid_india_gd/grid_events/2026-05-01
G00243 | 2026-05 | 74 | GD-1 | Jharkhand | JH | Eastern | 2026-05-04T16:53 | 2026-05-04T18:09 | 1.27 | 0 | 30 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Jharkhand 04-05-2026 16:53 04-05-2026 18:09 01:16 0 30 0.00% 0.14% 30682 21841 At 16:53 Hrs on 25/05/2026, Y-B-Earth fault occurred in 220kV Chatra -Latehar line and line got tripped from both ends, at the same time 220kV Chatra-Daltonganj line also tripped from Chatra end only, resulting 220 | 2 GD-1 Jharkhand 04-05-2026 16:53 04-05-2026 18:09 01:16 0 30 0.00% 0.14% 30682 21841 At 16:53 Hrs on 25/05/2026, Y-B-Earth fault occurred in 220kV Chatra -Latehar line and line got tripped from both ends, at the same time 220kV Chatra-Daltonganj line also tripped from Chatra end only, resulting 220kV Chatra S/s became dead. Total 30 MW load loss was reported at Chatra S/s. 220 KV Daltongunj- Chatra220 KV Latehar- Chatra | grid_india_gd/grid_events/2026-05-01
G00244 | 2026-05 | 52 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-04T19:54 | 2026-05-04T20:33 | 0.65 | 160 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Therefore, JP Bina Unit # 01 got tripped due to loss of evacuation path resulting in generation loss of 160 MW at JP Bina. | 6 GD-1 Madhya Pradesh 04-05-2026 19:54 04-05-2026 20:33 00:39 160 - 0.20% - 79350 69622 Complete outage of 400 kV JP Bina: 400 kV JAYPEE BINA – MPPTCL (Line #2) got tripped at 19:52 Hrs/04.05.2026 on Y-N fault. JAYPEE BINA – PGCIL BINA (Line #1) got tripped at 19:54 Hrs/04.05.2026 on Y-N fault. Therefore, JP Bina Unit # 01 got tripped due to loss of evacuation path resulting in generation loss of 160 MW at JP Bina. Heavy thunderstorm reported at that time which resulted in tripping of other 765 kV lines also in Bina region. U#2 was already out for boiler license renewal. 1. 400 KV JP Bina- Bina (PG)2. 400 KV JP Bina- Bina (MP)3. JP BINA Unit 1 (250 MW) | grid_india_gd/grid_events/2026-05-01
G00245 | 2026-05 | 53 | GD-1 | Maharashtra | MH | Western | 2026-05-05T18:55 | 2026-05-05T21:13 | 2.3 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GD-1 Maharashtra 05-05-2026 18:55 05-05-2026 21:13 02:18 - - - - 79675 66545 Complete outage of 220 kV Tandulwadi (Serentica): At 18:55 hrs / 05-05-2026, Busbar protection operated at 220 kV Tandulwadi substation during first-time charging (FTC) of 33 kV Bay-311 (Feeder-09) at Tandulwadi. This res | 7 GD-1 Maharashtra 05-05-2026 18:55 05-05-2026 21:13 02:18 - - - - 79675 66545 Complete outage of 220 kV Tandulwadi (Serentica): At 18:55 hrs / 05-05-2026, Busbar protection operated at 220 kV Tandulwadi substation during first-time charging (FTC) of 33 kV Bay-311 (Feeder-09) at Tandulwadi. This resulted and tripping of both 220 kV Tandulwadi-Bus-1&2 buses and 220 kV Tandulwadi substation became dark. No generation or load loss occurred during the event. 1. 220 kV Kallam-Tandulwadi-1 2. 220/33 kV Tandulwadi-ICT-1 3. 220/33 kV Tandulwadi-ICT-2 | grid_india_gd/grid_events/2026-05-01
G00246 | 2026-05 | 54 | GD-1 | Gujarat | GJ | Western | 2026-05-06T19:45 | 2026-05-07T00:01 | 4.27 | 90 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Tripping of the evacuation line resulted in blackout of the 220/33 kV AEPL Nanavalka Wind Power Plant, leading to a generation loss of approximately 90 MW. | 8 GD-1 Gujarat 06-05-2026 19:45 07-05-2026 00:01 04:16 90 - 0.11% - 83186 71485 Complete outage of 220 kV Nanavalka (Alfanar): At 19:45 Hrs/06.05.2026, the 220 kV Nanavalka–Bhuj transmission line tripped on B-E fault due to foreign conducting material thrown by unknown person. Tripping of the evacuation line resulted in blackout of the 220/33 kV AEPL Nanavalka Wind Power Plant, leading to a generation loss of approximately 90 MW. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C | grid_india_gd/grid_events/2026-05-01
G00247 | 2026-05 | 75 | GD-1 | Odisha | OD | Eastern | 2026-05-07T11:03 | 2026-05-07T11:34 | 0.52 | 0 | 95 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GD-1 Odisha 07-05-2026 11:03 07-05-2026 11:34 00:31 0 95 0.00% 0.41% 3222 23368 Prior to the disturbance 220 kV Bus-1 & 400/220 kV ICT-1 at 220 kV New Duburi S/S was under planned S/D. At 11:03 Hrs during isolator operation for restoration of 400/220kV 315 MVA ICT-1, a bus fault occurred in 220kV | 3 GD-1 Odisha 07-05-2026 11:03 07-05-2026 11:34 00:31 0 95 0.00% 0.41% 3222 23368 Prior to the disturbance 220 kV Bus-1 & 400/220 kV ICT-1 at 220 kV New Duburi S/S was under planned S/D. At 11:03 Hrs during isolator operation for restoration of 400/220kV 315 MVA ICT-1, a bus fault occurred in 220kV Bus-2 which led to bus bar protection operation of 220kV bus-2 at New Duburi S/s and all elements connected through bus-2 got tripped. 220kV New Duburi S/s became dead. Total load loss of 95 MW reported at Duburi S/s. 400KV/220KV 315 MVA ICT 2 & 3 AT NEW DUBURI 220kV Main bus 2 220KV New Duburi-OLD DUBURI-I & II 220KV New Duburi-BHADRAK 220KV New Duburi-BALIMUNDA 220KV New Duburi-BALICHANDRAPUR 220KV New Duburi-PARADEEP 220KV New Duburi-JINDAL-I & II 220KV New Duburi-ROHIT(TSL) 220KV New Duburi-VISA-1 & 2 220KV New Duburi-MAITHAN 220KV New Duburi-NU VISTA | grid_india_gd/grid_events/2026-05-01
G00248 | 2026-05 | 55 | GD-1 | Gujarat | GJ | Western | 2026-05-07T18:59 | 2026-05-07T21:27 | 2.47 | 163 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to the loss of the evacuation path, a generation loss of 163 MW occurred at the 220/33 kV AEPL Nana Valka Substation. | 9 GD-1 Gujarat 07-05-2026 18:59 07-05-2026 21:27 02:28 163 - 0.20% - 81779 68791 Complete outage of 220 kV Nanavalka (Alfanar): At 18:59 hrs/07-05-2026, the 220 kV Nanavalka–Alfanar–Bhuj-1 transmission line tripped at Alfanar end only and A/R susseful at Bhuj end due to a B-phase to Earth fault due to foreign conducting material thrown by unknown person. Due to the loss of the evacuation path, a generation loss of 163 MW occurred at the 220/33 kV AEPL Nana Valka Substation. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C Elements Tripped Details of Grid Events during the Month of May 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of May 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in | grid_india_gd/grid_events/2026-05-01
G00249 | 2026-05 | 6 | GD-1 | Rajasthan | RJ | Northern | 2026-05-08T09:25 | 2026-05-08T10:27 | 1.03 | 0 | 413 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 6 GD-1 Rajasthan 08-05-2026 09:25 08-05-2026 10:27 01:02 0 413 0.00% 73.07% 58195 56520 i)400/220kV Hindaun(RS) and 400/220kV Alwar(RS) have one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. 400 KV Alwar(ATIL)-Hindaun(RS) (ATIL) Ckt is the only 400kV element connected to 400 KV Alwar(ATIL). ii)As reported, at 09:25 hrs, Y-B phase to phase fault occurred due to opening of isolator on charged condition during bus changeover shutdown activity (exact nature and location of fault yet to be shared). iii)Busbar protection at 400kV Hindaun(RS) was not in working condition. iv)On this fault, all 400kV lines connected at Hindaun(RS) tripped from remote end only sensing the fault in zone-2, no tripping occurred at Hindaun end (as reported). v)Due to this, complete blackout occurred at both 400/220kV Hindaun(RS) and 400/220kV Alwar(RS) S/s. vi)As per PMU at Heerapura (RS), Y-B phase to phase fault was observed with delayed fault clearance time of 520 ms. vii)As per SCADA, change in demand of approx 413 MW was observed in Rajasthan control area. 1) 400 KV Hindaun(RS)-Chhabra(RVUN) (RS) Ckt 2) 400 KV Heerapura-Hindaun (RS) Ckt 3) 400 KV Alwar(ATIL)-Hindaun(RS) (ATIL) Ckt Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / l | grid_india_gd/grid_events/2026-05-01
G00250 | 2026-05 | 56 | GD-1 | Maharashtra | MH | Western | 2026-05-08T12:24 | 2026-05-08T15:38 | 3.23 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Maharashtra 08-05-2026 12:24 08-05-2026 15:38 03:14 - - - - 79912 70035 Complete outage of 220 kV Tandulwadi (Serentica): At 12:24 hrs / 08-05-2026, Busbar protection operated at 220 kV Tandulwadi substation during Overcurrent protection operation in same 33 kV Bay-311 (Feeder-09) at Tandulw | 10 GD-1 Maharashtra 08-05-2026 12:24 08-05-2026 15:38 03:14 - - - - 79912 70035 Complete outage of 220 kV Tandulwadi (Serentica): At 12:24 hrs / 08-05-2026, Busbar protection operated at 220 kV Tandulwadi substation during Overcurrent protection operation in same 33 kV Bay-311 (Feeder-09) at Tandulwadi. This resulted and tripping of both 220 kV Tandulwadi-Bus-1&2 buses and 220 kV Tandulwadi substation became dark. No generation or load loss occurred during the event. 1. 220 kV Kallam-Tandulwadi-1 2. 220/33 kV Tandulwadi-ICT-1 3. 220/33 kV Tandulwadi-ICT-2 | grid_india_gd/grid_events/2026-05-01
G00251 | 2026-05 | 7 | GD-1 | Rajasthan | RJ | Northern | 2026-05-08T18:02 | 2026-05-08T21:20 | 3.3 | 0 | 375 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GD-1 Rajasthan 08-05-2026 18:02 08-05-2026 21:20 03:18 0 375 0.00% 62.52% 47129 59981 i)220kV Kushkhera(RS) has double main bus scheme. ii)During antecedent condition, 220kV Neemrana(PG)-Kushkhera(RS) (RS) Ckt and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt were carrying 102 MW & 111 MW respectively | 7 GD-1 Rajasthan 08-05-2026 18:02 08-05-2026 21:20 03:18 0 375 0.00% 62.52% 47129 59981 i)220kV Kushkhera(RS) has double main bus scheme. ii)During antecedent condition, 220kV Neemrana(PG)-Kushkhera(RS) (RS) Ckt and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt were carrying 102 MW & 111 MW respectively. iii)As reported, at 18:02hrs, isolator clamp/ jumper snapped of Main Bus-II R-ph isolator at Kushkhera end of 220 KV Neemrana(PG)-Kushkhera (RS) (RS) Ckt and created bus fault. iv)On this fault, bus bar protection (Z-I&II) operated and leading to tripping of all the elements connected at 220kV Kushkhera(RS). (Reason of tripping of both the 220kV bus yet to be received). v)As per PMU at Neemrana(PG), R-N phase to earth fault was observed with fault clearing time of 80ms. vi)As per SCADA, change in demand of approx 375 MW in Rajasthan control area is observed. 1) 220 KV Neemrana(PG)-Kushkhera (RS) (RS) Ckt 2) 220 KV Bhiwadi(PG)-Kushkhera (RS) (RS) Ckt 3) 220 KV Karoli(RS)-Kushkhera (RS) (RS) Ckt 4) 220 KV KG Basss(RS)-Kushkhera (RS) (RS) Ckt | grid_india_gd/grid_events/2026-05-01
G00252 | 2026-05 | 57 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-11T17:07 | 2026-05-11T19:43 | 2.6 | 35 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 35MW occurred at 220 kV Shajapur S/S due loss of evacuation path. | 11 GD-1 Madhya Pradesh 11-05-2026 17:07 11-05-2026 19:43 02:36 35 - 0.04% - 92005 76500 Complete outage of 220kV Shajapur Unit 8 (Taletuttayi):At 17:07 hrs/11.05.2026, 220kV Shajapur–Pachora Line (Unit-08) tripped on Y-phase to earth fault from both ends due to operation of differential protection in Y- phase. Generation loss of 35MW occurred at 220 kV Shajapur S/S due loss of evacuation path. 1. 220kV Pachora-Shajapur Unit-08- (Taletuttayi) | grid_india_gd/grid_events/2026-05-01
G00253 | 2026-05 | 9 | GI-1 | Uttarakhand | UK | Northern | 2026-05-12T12:58 | 2026-05-12T13:34 | 0.6 | 0 | 190 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-1 Uttarakhand 12-05-2026 12:58 12-05-2026 13:34 00:36 0 190 0.00% 29.26% 65033 64935 i)During antecedent condition, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 was carrying 113 MW from Roorkee(PG) to Roorkee(UK). ii)As reported, at 12:58 hrs, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 trippe | 9 GI-1 Uttarakhand 12-05-2026 12:58 12-05-2026 13:34 00:36 0 190 0.00% 29.26% 65033 64935 i)During antecedent condition, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 was carrying 113 MW from Roorkee(PG) to Roorkee(UK). ii)As reported, at 12:58 hrs, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 tripped on Y-N Phase to earth fault with fault distance of 13.37km from Roorkee(UK) end. As per DR, fault current was ~2.34kA from Roorkee(UK) end, fault clearing time was ~1s; fault sensed in zone-3 at Roorkee(UK) end (exact reason, nature and location of fault yet to be shared). iii)During the same time, tripping occurred at 132kV Laksar, Bhagwanpur and Churiyaal S/s (exact details of tripping yet to be received). iv)As per PMU at Roorkee(PG), Y-N Phase to earth fault was observed with fault clearance time of 80 ms. v)As per SCADA, change in demand of approx 190 MW in UƩarakhand control area was observed. 1) 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 | grid_india_gd/grid_events/2026-05-01
G00254 | 2026-05 | 10 | GI-2 | Rajasthan | RJ | Northern | 2026-05-12T14:13 | 2026-05-12T21:01 | 6.8 | 1575 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | iii)As per SCADA, change in NR solar generation of approx 1575 MW was observed among which 320 MW change observed in Rajasthan Solar . | 10 GI-2 Rajasthan 12-05-2026 14:13 12-05-2026 21:01 06:48 1575 0 239.11% 0.00% 65869 66192 i)As reported at 14:13 hrs, 765 KV Sikar_2(PSTL)-Aligarh(PG) (PASTL) Ckt-2 tripped on R-B-N double phase to earth fault with fault current of Ir=~7.65kA, Iy=~6.94kA from Aligarh(PG) end; fault sensed in zone-1 at Aligarh end (exact reason, nature and location of fault yet to be shared). ii)As per PMU at Sikar2(PG), R-B-N double phase to earth fault was observed with fault clearing time of 80 ms. Voltage dipped upto 0.564 pu. iii)As per SCADA, change in NR solar generation of approx 1575 MW was observed among which 320 MW change observed in Rajasthan Solar . 1) 765 KV Sikar_2(PSTL)-Aligarh(PG) (PASTL) Ckt-2 | grid_india_gd/grid_events/2026-05-01
G00255 | 2026-05 | 8 | GD-1 | Haryana | HR | Northern | 2026-05-12T23:03 | 2026-05-13T01:31 | 2.47 | 0 | 128 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GD-1 Haryana 12-05-2026 23:03 13-05-2026 01:31 02:28 0 128 0.00% 17.51% 60567 73095 i)220/132kV Isherwal(HR) has double main bus scheme at both 220kV level 132kV level. ii)During antecedent condition, 220kV Isherwal-Sagwan Ckt-1 & 2 were out of service and 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) | 8 GD-1 Haryana 12-05-2026 23:03 13-05-2026 01:31 02:28 0 128 0.00% 17.51% 60567 73095 i)220/132kV Isherwal(HR) has double main bus scheme at both 220kV level 132kV level. ii)During antecedent condition, 220kV Isherwal-Sagwan Ckt-1 & 2 were out of service and 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 & 2 were carrying approx 56 MW each (as per SCADA). iii)As reported, at 23:03 hrs, R phase Jumper of Tower No. 177 snapped of 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 and line tripped on R-Y phase to phase fault with fault current of Ir=~5.15kA & Iy=~2.44kA and fault distance of 8.5km from Isherwal end. From SCADA SOE, it seems that line auto-reclosed from Bhiwani(PG) end (confirmation yet to be received from POWERGRID). iv)During the same time, 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-2 also tripped from Bhiwani end sensing this fault in zone-2 (exact reason and nature of protection operation yet to be shared). v)Due to tripping of both 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 & 2, complete blackout occurred at 220/132kV Isherwal(HR) S/s. vi)As per PMU at Bhiwani(PG), R-Y phase to phase fault was observed with fault clearing time of 120 ms. vii)As per SCADA, change in demand of approx 128 MW was observed at Haryana Control area. 1) 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-1 2) 220 KV Bhiwani (PG)-Isherwal(HR) (HVPNL) Ckt-2 | grid_india_gd/grid_events/2026-05-01
G00256 | 2026-05 | 14 | GD-1 | Delhi | DL | Northern | 2026-05-13T10:58 | 2026-05-13T11:19 | 0.35 | 0 | 195 | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GD-1 Delhi 13-05-2026 10:58 13-05-2026 11:19 00:21 0 195 0.00% 28.46% 64619 68529 i)During antecedent condition, 220kV Peeragarhi-Mundka (DTL) Ckt-1 & 2 were feeding load of 220kV Peeragrhi and Wazipur S/s. ii)As reported, at 10:28 hrs, all elements of 220 kV Peeragarhi(DTL) S/s tripped while tak | 14 GD-1 Delhi 13-05-2026 10:58 13-05-2026 11:19 00:21 0 195 0.00% 28.46% 64619 68529 i)During antecedent condition, 220kV Peeragarhi-Mundka (DTL) Ckt-1 & 2 were feeding load of 220kV Peeragrhi and Wazipur S/s. ii)As reported, at 10:28 hrs, all elements of 220 kV Peeragarhi(DTL) S/s tripped while taking 220/33 kV 100MVA ICT-3 at Peeragarhi(DTL) for planned outage (exact reason of tripping yet to be shared). iii)Due to tripping of 220kV Peeragarhi-Mundka (DTL) Ckt-1 & 2, load of 220kV Peeragrhi and Wazipur S/s got affected. iv)As per PMU at Mandola(PG), no fault was observed in the system. v)As per SCADA, change in demand of approx 285 MW in Delhi control area was observed. However, as reported by SLDC Delhi load loss of approx. 195 MW occurred in Delhi control area. vi)Load of 220kV Wazipur S/s was normalised through 220kV Wazipur-Shalimarbagh (DTL) Ckt-1. 1) 220kV Peeragarhi-Mundka (DTL) Ckt-1 2) 220kV Peeragarhi-Mundka (DTL) Ckt-2 3) 220kV Peeragarhi-Wazipur (DTL) Ckt-1 4) 220kV Peeragarhi-Wazipur (DTL) Ckt-2 5) 220/33 kV 100MVA ICT-1 at Peeragarhi(DTL) 6) 220/33 kV 100MVA ICT-2 at Peeragarhi(DTL) | grid_india_gd/grid_events/2026-05-01
G00257 | 2026-05 | 59 | GD-1 | Gujarat | GJ | Western | 2026-05-13T14:09 | 2026-05-13T14:49 | 0.67 | 8963 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GD-1 Gujarat 13-05-2026 14:09 13-05-2026 14:49 00:40 8963 - 9.44% - 94959 77710 Complete outage of Khavda Complex: Grid disturbance occurred at pooling stations KPS1, KPS2, KPS3 at around 14:09 Hrs on 13.05.2026 leading to total generation loss of 8963 MW in Khavda Complex. | 13 GD-1 Gujarat 13-05-2026 14:09 13-05-2026 14:49 00:40 8963 - 9.44% - 94959 77710 Complete outage of Khavda Complex: Grid disturbance occurred at pooling stations KPS1, KPS2, KPS3 at around 14:09 Hrs on 13.05.2026 leading to total generation loss of 8963 MW in Khavda Complex. Prior to the incident, the grid parameters were stable and operating in normal limits. 1 765KV-KHAVDA PS-I-Bhuj-1 2 765KV/400KV KHAVDA PS-I-ICT-1, 2 4 400KV-KHAVDA PS-I-KHAVDA PSS6-1 5 765KV-KHAVDA PS-2-LAKADIA-1 6 400kV KHAVDA PS1-KHAVDA PSS-1 7 400kV KHAVDA PS1-KHAVDA PSS-13 8 400kV KHAVDA PS1-KHAVDA PSS-2 9 765KV-KHAVDA PS-I-KHAVDA PS-2-1 10 765KV/400KV KHAVDA PS-2-ICT-4 11 400kV Khavda PS I Bus Sectionaliser 12 400KV-KHAVDA PSS5-KHAVDA PS-I-1 13 765KV-KHAVDA PS-2-LAKADIA-2 14 400KV-KHAVDA PS-I-Khavda PSS4-1 15 400KV-KHAVDA PS-I-KhavdaPSS9-1 16 765KV/400KV KHAVDA PS-2-ICT-5 | grid_india_gd/grid_events/2026-05-01
G00258 | 2026-05 | 11 | GD-1 | Rajasthan | RJ | Northern | 2026-05-13T14:34 | 2026-05-13T15:22 | 0.8 | 495 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | , ~495 MW lost due to loss of evacuation path. | 11 GD-1 Rajasthan 13-05-2026 14:34 13-05-2026 15:22 00:48 495 0 77.26% 0.00% 64068 68453 i)400kV AGE25L RE station is connected at Bhadla2(PG) at 400kV level and its generation evacuates through 400 KV AGE25L SL_BHD2_PG-Bhadla_2 (PG) (AGE25L) Ckt. ii)During antecedent condition, 400kV AGE25L RE station was generating ~495MW (as per PMU). iii)As reported at 15:37 hrs, 400 KV AGE25L SL_BHD2_PG-Bhadla_2 (PG) (AGE25L) Ckt tripped on overvoltage stage-1 protection from Bhadla2(PG) end. DT received at AGE25L end as per DR. As reported by Adani, voltage reached ~1.06 pu at AGE25L end and ~1.11 pu at Bhadla2 end. iv)Due to tripping of line, complete generation of AGE25L i.e., ~495 MW lost due to loss of evacuation path. v)As per PMU at Bhadla2(PG), 3-phase fault was observed with fault clearing time of 80 ms followed by voltage rise upto ~1.11 pu. vi)As per PMU, solar generation loss of approx 495 MW occurred at AGE25L(IP). 1) 400 KV AGE25L SL_BHD2_PG-Bhadla_2 (PG) (AGE25L) Ckt | grid_india_gd/grid_events/2026-05-01
G00259 | 2026-05 | 58 | GD-1 | Chhattisgarh | CG | Western | 2026-05-13T16:16 |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 1704 MW occurred at JSW Mahanadi due to loss of evacuation path. | 12 GD-1 Chhattisgarh 13-05-2026 16:16 Line is Out NA 1704 - 1.79% - 95454 79424 Complete outage of 400kV JSW Mahanadi: At 16:16 hrs/13-05-2026, 400 kV JSW Mahanadi–Champa Ckt-3 and Ckt-4 tripped due to tower collapse caused by lightning and thunderstorm activity. Generation loss of 1704 MW occurred at JSW Mahanadi due to loss of evacuation path. JSW Mahanadi Units 2 to 4 also tripped which makes Station became dead. 1. 1 400kV-JSW Mahanadi-Champa ckt-3 2. 2 400kV-JSW Mahanadi-Champa ckt-4 3. 3 JSW Mahanadi Unit-2 4. JSW Mahanadi Unit-3 5. JSW Mahanadi Unit- 4 | grid_india_gd/grid_events/2026-05-01
G00260 | 2026-05 | 15 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-13T16:56 | 2026-05-13T19:33 | 2.62 | 0 | 110 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GD-1 Uttar Pradesh 13-05-2026 16:56 13-05-2026 19:33 02:37 0 110 0.00% 16.65% 55792 66083 i)During antecedent condition, 220 KV Phulpur(UP)-Jaunpur (UP) (PG) Ckt-1 were already out (as reported, line tripped at 16:41 hrs on B-N phase to earth fault with fault distance of 2.775km and fault current | 15 GD-1 Uttar Pradesh 13-05-2026 16:56 13-05-2026 19:33 02:37 0 110 0.00% 16.65% 55792 66083 i)During antecedent condition, 220 KV Phulpur(UP)-Jaunpur (UP) (PG) Ckt-1 were already out (as reported, line tripped at 16:41 hrs on B-N phase to earth fault with fault distance of 2.775km and fault current of 5.734kA from Phulpur end). 220kV Phulpur-Aurai Ckt and 220kV Phulpur-Pratapgarh Ckt were also out of service. Only 220 KV Allahabad(PG)-Phulpur(UP) (UP) Ckt-1 was in service at 220kV Phulpur. ii)As reported, at 16:56 hrs, 220 KV Allahabad(PG)-Phulpur(UP) (UP) Ckt-1 tripped on R-N phase to earth fault (exact location of fault yet to be received). As per DR at Allahabad(PG) end, fault current was ~3.164kA from Allahabad(PG); Zone-2 operated at Allahabad end; fault clearing time=~400 ms. iii)Due to this tripping, complete blackout occurred at 220/132kV Phulpur(UP) S/s. iv)As per PMU at Varanasi(PG), R-B phase to phase fault followed by R-N Phase to earth fault was observed with fault clearance time of 120 ms and 400 ms (delayed) respectively. v)As per SCADA, change in demand of approx 110 MW in UƩar Pradesh control area was observed. 1 )220 KV Phulpur(UP)-Jaunpur (UP) (PG) Ckt-1 2) 220 KV Allahabad(PG)-Phulpur(UP) (UP) Ckt-1 | grid_india_gd/grid_events/2026-05-01
G00261 | 2026-05 | 13 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-13T16:59 | 2026-05-13T19:11 | 2.2 | 0 | 200 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Allahabad(PG)-Jhusi(UP) (PG) Ckt 2) 220 KV Jaunpur-Jhusi(UP) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. | 13 GD-1 Uttar Pradesh 13-05-2026 16:59 13-05-2026 19:11 02:12 0 200 0.00% 30.38% 55431 65828 i)During antecedent condition, 220 KV Allahabad(PG)-Jhusi(UP) (PG) Ckt and 220 KV Jaunpur-Jhusi(UP) Ckt were carrying approx 20 MW and 10 MW respectively (as per SCADA). ii)As reported, at 16:59 hrs, 220 KV Allahabad(PG)-Jhusi(UP) (PG) Ckt tripped on Y-N Phase to earth fault with fault distance of 25.7km from Allahabad(PG) end. As per DR, Fault current was Iy=~6.484kA from Allahabad(PG) end with fault clearing time of ~400 ms; Zone-2 operated at Allahabad end. iii)During the same time, 220 KV Jaunpur-Jhusi(UP) Ckt also tripped (exact reason and nature of protection operated yet to be received). iv)Due to tripping of both the elements, complete blackout occurred at 220/132kV Jhusi(UP) S/s. v)As per PMU at Varanasi(PG), Y-N Phase to earth fault was observed with delayed fault clearance time of 400 ms. vi)As per SCADA, change in demand of approx 200 MW in UƩar Pradesh control area was observed. 1) 220 KV Allahabad(PG)-Jhusi(UP) (PG) Ckt 2) 220 KV Jaunpur-Jhusi(UP) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % | grid_india_gd/grid_events/2026-05-01
G00262 | 2026-05 | 12 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-13T17:52 | 2026-05-13T19:13 | 1.35 | 0 | 100 | FALSE | TRUE | FALSE | FALSE | TRUE | ii)As reported, at 17:52 hrs, 400 KV Jaunpur -Obra_B (UP) Ckt-1, 400 KV Jaunpur -Obra_C_TPS (UP) Ckt-1 and 400/220 KV 315 MVA ICT-3 at Jaunpur(UP) tripped due to storm accompanied by gusty wind. | 12 GD-1 Uttar Pradesh 13-05-2026 17:52 13-05-2026 19:13 01:21 0 100 0.00% 16.09% 49124 62132 i)During antecedent condition, 400 KV Jaunpur (UP)-Varanasi(PG) (UP) Ckt-1 & 2 were already out (as per DR at Varanasi end of 400 KV Jaunpur (UP)-Varanasi(PG) (UP) Ckt-1, line tripped at 17:37 hrs on Y-N Phase to earth fault (Iy=~25kA) followed by by Y-B-N double Phase to earth fault (Iy=~31kA, Ib=~28.9kA) after ~1 s during A/R operation with fault distance of 3.13km from Varanasi end; Zone-1 operated at Varanasi end). ii)As reported, at 17:52 hrs, 400 KV Jaunpur -Obra_B (UP) Ckt-1, 400 KV Jaunpur -Obra_C_TPS (UP) Ckt-1 and 400/220 KV 315 MVA ICT-3 at Jaunpur(UP) tripped due to storm accompanied by gusty wind. As per DR at Obra_C end, Y-N fault (Iy=~3.39kA) with unsuccessful A/R (Iy=~3.63kA) was observed; Zone-1 operated at Obra_C end. iii)Due to tripping of all these elements, complete blackout occurred at 400/220kV Jaunpur(UP) S/s. iv)As per PMU at Varanasi(PG), Y-N Phase to earth fault with unsuccessful A/R was observed with fault clearance time of 120 ms. v)As per SCADA, change in demand of approx 125 MW in UƩar Pradesh control area was observed. As reported by SLDC UP , load loss of approx 100 MW occurred. 1) 400 KV Jaunpur (UP)-Varanasi(PG) (UP) Ckt-1 2) 400 KV Jaunpur (UP)-Varanasi(PG) (UP) Ckt-2 3) 400 KV Jaunpur -Obra_B (UP) Ckt-1 4) 400 KV Jaunpur -Obra_C_TPS (UP) Ckt-1 5) 400/220 KV 315 MVA ICT-3 at Jaunpur(UP) | grid_india_gd/grid_events/2026-05-01
G00263 | 2026-05 | 16 | GD-1 | Rajasthan | RJ | Northern | 2026-05-14T08:17 | 2026-05-14T09:14 | 0.95 | 0 | 345 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GD-1 Rajasthan 14-05-2026 08:17 14-05-2026 09:14 00:57 0 345 0.00% 61.91% 52634 55730 i) 220 kV GSS Heerapura has four 220 kV buses. Bus-A and Bus-B are interconnected through a bus sectionaliser.ii) Prior to the incident, Chomu, VKIA, and Kotputli feeders were operating from Bus-G.iii) At 08:17 | 16 GD-1 Rajasthan 14-05-2026 08:17 14-05-2026 09:14 00:57 0 345 0.00% 61.91% 52634 55730 i) 220 kV GSS Heerapura has four 220 kV buses. Bus-A and Bus-B are interconnected through a bus sectionaliser.ii) Prior to the incident, Chomu, VKIA, and Kotputli feeders were operating from Bus-G.iii) At 08:17 hrs, the R-phase CT of the 220 kV Bus Sectionaliser A-B (Bus-A side) burst, damaging the associated CB pole and opposite-side CT. The fault initiated as an R-phase fault and subsequently evolved into a three-phase fault.iv) The 220 kV Heerapura–Niwana circuit tripped on Reverse Zone-4 protection. Simultaneously, the main DCDB fuse blew, causing loss of DC supply and rendering station protection relays inoperative.v) Consequently, all feeders connected to Bus-A and Bus-B tripped from remote ends on Zone-2 distance protection.vi) Due to loss of DC supply, Bus Coupler B-C failed to trip, keeping Bus-D and Bus-E interconnected.vii) As a result, all feeders connected to Bus-D and Bus-E tripped on remote Zone-2 protection, while connected transformers tripped on O/C and E/F protection.viii) The 400/220 kV, 500 MVA ILT-5, operating on Bus-F with the 220 kV NPH line, contributed fault current through the 132 kV NPH–Heerapura line and 220/132 kV Transformer-3 to the faulty Bus-B.ix) Consequently, 220/132 kV Transformers-1 & 2 and the 132 kV NPH–Heerapura line at NPH tripped, resulting in a complete blackout at 220 kV NPH substation.x) Simultaneously, 400 kV Phagi–Heerapura Ckt-2 tripped on | grid_india_gd/grid_events/2026-05-01
G00264 | 2026-05 | 17 | GD-1 | Rajasthan | RJ | Northern | 2026-05-15T11:06 | 2026-05-15T12:55 | 1.82 | 830 | 625 | TRUE | FALSE | FALSE | FALSE | TRUE | Solar generation loss of approx 702 MW at Essel RPSS (IP) and 128 MW at Azure34(IP) occurred. | 17 GD-1 Rajasthan 15-05-2026 11:06 15-05-2026 12:55 01:49 830 625 131.83% 93.94% 62960 66532 i)220 kV Essel RPSS(IP) and 220kV Azure Power34(IP) RE stations are connected at Bhadla(PG) at 220kV level and their generation evacuates through 220 KV Bhadla(PG)- ESUCRL RPSS (ESUCRL) Ckt-1 & 2 and 220 KV Bhadla(PG)-Azure Power34 (APTFL) Ckt. ii)During antecedent condition, 220 kV Essel RPSS(IP) and 220kV Azure Power34(IP) were generating approx 702 MW and 128 MW respectively (total 830 MW) (as per PMU). iii)As reported at 11:06 hrs, 220 KV Bhadla(PG)-ESUCRL RPSS (ESUCRL) Ckt-1 tripped due to a broken R-phase jumper (exact reason, nature and location of fault yet to be shared). As a consequence of this tripping, ESUCRL_SL internal elements/lines at MSS and ISS-1 & 2 also tripped resulting into complete blackout at 220 kV Essel RPSS(IP) S/s. iv)During the same time, 220/33 kV 130 MVA ICT 1 at Azure Power 34 Solar(APTFL) also tripped on differential protection operation (exact reason of tripping yet to be shared) resulting into complete blackout at 220kV Azure Power34(IP) S/s. v)As per PMU at Bhadla(PG), frequency dropped from 49.995 Hz to 49.785 Hz within 8 s. As a result, df/dt protection operated in Punjab. As per SCADA, change in demand of approx 625 MW was observed in Punjab control area and load normalised at ~11:20 hrs. vi)As per PMU, R-Y phase to phase fault was observed with fault clearing time of 80 ms. Solar generation loss of approx 702 MW at Essel RPSS (IP) and 128 MW at | grid_india_gd/grid_events/2026-05-01
G00265 | 2026-05 | 60 | GD-1 | Maharashtra | MH | Western | 2026-05-15T16:47 | 2026-05-15T18:02 | 1.25 | 32 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GD-1 Maharashtra 15-05-2026 16:47 15-05-2026 18:02 01:15 32 - 0.04% - 90984 76009 Complete outage of 220 kV Jaulala (Renew power): At 16:47 hrs/15-05-2026, 220 kV Jaulala–Kallam line tripped at Jaulala end due to an extended R-phase earth fault. The fault occurred following damage to the Lightnin | 14 GD-1 Maharashtra 15-05-2026 16:47 15-05-2026 18:02 01:15 32 - 0.04% - 90984 76009 Complete outage of 220 kV Jaulala (Renew power): At 16:47 hrs/15-05-2026, 220 kV Jaulala–Kallam line tripped at Jaulala end due to an extended R-phase earth fault. The fault occurred following damage to the Lightning Arrester (LA) of 33 kV Feeder-4 caused by severe gusty winds, heavy rain, and lightning activity. Protections 86A & 86B operated successfully. 1. 220 kV Jaulala - Kallam 2. 220 kV Jaulala Bus-1 3. 220 kV Jaulala Bus-2 | grid_india_gd/grid_events/2026-05-01
G00266 | 2026-05 | 61 | GD-1 | Chhattisgarh | CG | Western | 2026-05-16T19:30 | 2026-05-16T20:48 | 1.3 | 1153 |  | FALSE | FALSE | FALSE | FALSE | FALSE | However, at 19:30 hrs, Unit-2 also tripped on low boiler air flow, resulting in a total generation loss of 1153 MW and complete blackout of the substation. | 15 GD-1 Chhattisgarh 16-05-2026 19:30 16-05-2026 20:48 01:18 1153 - 1.35% - 85186 73085 Complete outage of 400 KV APL Raipur/REL: At 18:44 hrs/16.05.2026, the 400 kV APL Raipur (REL) – Durg Line-1 tripped on an R-phase to Earth (R-E) fault during inclement weather conditions, including heavy rain and lightning activity in the Chhattisgarh region. Subsequently, at 18:50 hrs, the 400 kV APL Raipur (REL) – Durg Line-2 tripped during reclaim time on a Y-phase to Earth (Y-E) fault. Following the tripping of both transmission lines, APL Raipur (REL) Unit-1 (685 MW) tripped at 18:52 hrs on “Boiler All Fuel Off” protection, while Unit-2 (685 MW) continued operating in islanded mode supplying internal auxiliary load. However, at 19:30 hrs, Unit-2 also tripped on low boiler air flow, resulting in a total generation loss of 1153 MW and complete blackout of the substation. Power supply to the plant auxiliaries was subsequently restored at 20:48 hrs through restoration of the 400 kV APL Raipur (REL) – Durg Line-2. 1. 1. 400 kV APL Raipur Durg 1 18:44 2. 2 400 kV APL Raipur Durg 2 18:50 3. 3 400 kV APL Raipur Unit 1 18:52 4. 4 400 kV APL Raipur Unit 2 19:30 5. 5 400 kV APL Raipur Bus 1 19:30 6. 400 kV APL Raipur Bus 2 19:30 | grid_india_gd/grid_events/2026-05-01
G00267 | 2026-05 | 62 | GI-1 | Gujarat | GJ | Western | 2026-05-16T19:40 | 2026-05-18T15:05 | 43.42 | 151 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to bus tripping, ALTPS-GEB generating station became dark, resulting in generation loss of 151 MW.220Kv Bhachunda Akri mota line tripped due B phase CVT Fail at 220Kv Akri mota end. | 16 GI-1 Gujarat 16-05-2026 19:40 18-05-2026 15:05 43:25 151 - 0.18% - 85572 72913 Partially outage of 220kV ALTPS-GEB: At 19:40 hrs/16-05-2026, 220 kV Akrimota–Nakhatrana line tripped due to conductor snapping, which subsequently led to tripping of the 220 kV bus at Akrimota GEB (ALTPS) power plant. At the time of the incident, 220 kV Akrimota–Bhachunda line and another circuit of 220 kV Akrimota–Nakhatrana line were already under planned outage. Due to bus tripping, ALTPS-GEB generating station became dark, resulting in generation loss of 151 MW.220Kv Bhachunda Akri mota line tripped due B phase CVT Fail at 220Kv Akri mota end.Bph CVT Fail at 220Kv Akri mota end.trial taken at 20:15 from 400kv Bhachunda end but Bphase missing observed at 220Kv Akri mota end so line kept in PF.Conductor snapped between location no.299 to 300. Z2 optd at 220KN Nakhatrana end. PLCC Carrier protection is not in service at 220KV Akrimota ss. 1. 220KV Akrimota-Nakhatrana 2. 220KV Akrimota-Bhachunda | grid_india_gd/grid_events/2026-05-01
G00268 | 2026-05 | 63 | GD-1 | Gujarat | GJ | Western | 2026-05-17T19:51 | 2026-05-17T22:54 | 3.05 | 104 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Since 220 kV Baranda and 220 kV Kotda Math RE Plants were connected to the same bus section, generation loss of 49 MW at Baranda RE Plant and 55 MW at Kotda Madh RE Plant occurred. | 17 GD-1 Gujarat 17-05-2026 19:51 17-05-2026 22:54 03:03 104 - 0.12% - 83289 71102 Complete outage of 220 kV Baranda (Avikiran) & Kotda madha (Alfanar): At 19:51 Hrs/17.05.2026, the 220 kV Bhuj–Baranda ASIPL-1 line tripped on B-phase to Earth (B-E) fault. Subsequently, 220 kV Bhuj Bus-2 Section-C tripped due to operation of LBB protection of Bay-232 associated with the 220 kV Baranda line bay, caused by non-clearance of the fault. Since 220 kV Baranda and 220 kV Kotda Math RE Plants were connected to the same bus section, generation loss of 49 MW at Baranda RE Plant and 55 MW at Kotda Madh RE Plant occurred. Line patrolling was completed at 00:18 Hrs on 18.05.2026, and no abnormality was observed on the line during patrolling. The line was proposed for test charging; however, the POWERGRID team denied charging due to LBB operation of Bay-232 breaker. 1. 220 kV Baranda Bhuj 2. 220 kV Kotda Math Bhuj 3. 220 kV Bhuj Bus 2 Section C 4. 400/220 kV Bhuj ICT 8 5. 400/220 kV Bhuj ICT 9 6. 220 kV Bhuj Bus coupler Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of May 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Ge | grid_india_gd/grid_events/2026-05-01
G00269 | 2026-05 | 19 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-18T00:49 | 2026-05-18T02:59 | 2.17 | 0 | 90 | FALSE | FALSE | FALSE | FALSE | FALSE | 19 GD-1 Uttar Pradesh 18-05-2026 00:49 18-05-2026 02:59 02:10 0 90 0.00% 12.08% 57991 74488 i)220/132kV Bachravan(UP) has double main and transfer bus scheme at 220kV level and single main and transfer bus scheme at 132kV level.ii)During antecedent condition, 220 KV Raebareilly(PG)-Bachravan(UP) (PG | 19 GD-1 Uttar Pradesh 18-05-2026 00:49 18-05-2026 02:59 02:10 0 90 0.00% 12.08% 57991 74488 i)220/132kV Bachravan(UP) has double main and transfer bus scheme at 220kV level and single main and transfer bus scheme at 132kV level.ii)During antecedent condition, 220 KV Raebareilly(PG)-Bachravan(UP) (PG) Ckt and 220 KV Bijnaur-Bachravan(UP) (UP) Ckt were carrying ~151 MW (from Raebareilly(PG) to Bachravan(UP)) and ~96 MW (from Bachravan(UP) to Bijnaur).iii)As reported, at 00:49 hrs, LV side CB of 220/132kV 160 MVA ICT-2 at Bachravan(UP) tripped due to damage of R phase PT of 132kV Main Bus at 220kV Bachravan(UP) S/s which further led to insulator disc flashover at 132kV bus.iv)During the same time, 220 KV Raebareilly(PG)-Bachravan(UP) (PG) Ckt and 220 KV Bijnaur-Bachravan(UP) (UP) Ckt tripped on zone-3 from Raebareilly(PG) and Bijnaur end respectively sensing the fault. As per DR at Raebareilly(PG) end, R-N fault (Ir=~2.86kA) converted to R-Y-N fault (Ir=~2.53kA, Iy=~2.39kA) was observed.v)Due to tripping of all these elements, complete blackout occurred at i)220/132kV Bachravan(UP) S/s.vi)As per PMU at Unchahar(NT), R-N fault converted to R-Y-N fault was observed with delayed fault clearance time of 840 ms.vii)As per SCADA, change in demand of approx 125 MW in Uttar Pradesh control area was observed. As reported by SLDC UP, load loss of approx 90 MW occurred. 1) 220 KV Raebareilly(PG)-Bachravan(UP) (PG) Ckt 2) 220 KV Bijnaur-Bachravan(UP) (UP) Ckt 3) 220/132kV 160 MVA ICT-1 at B | grid_india_gd/grid_events/2026-05-01
G00270 | 2026-05 | 18 | GD-1 | Uttarakhand | UK | Northern | 2026-05-18T12:57 | 2026-05-20T13:12 | 48.25 | 347 | 50 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, generation loss of approx 85 MW at Alaknanda HEP and 262 MW at Vishnuprayag HEP was observed. | 18 GD-1 Uttarakhand 18-05-2026 12:57 20-05-2026 13:12 00:15 347 50 50.31% 6.58% 68972 76020 i)Power of 82.5*4 MW Alaknanda HEP, 100*4MW Vishnuprayag HEP and 33*3MW Singoli Bhatwari HEP evacuates through 400 KV Alaknanda GVK (UPC)-Muzaffarnagar(UP) ckt and 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) ckt.ii)During antecedent condition, 82.5 MW Alaknanda HEP – UNIT 3 and 110 MW Vishnuparyag HPS - UNIT 1, 3 & 4 were on running condition and were generating approx 85 MW, 100 MW, 81 MW and 81 MW respectively and 220kV Singoli Bhatwari had no generation. 400kV Alaknanda(UP)-Srinagar(UK) Ckt-2 was already under shutdown since 23.03.2026. 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt tripped at 12:07 hrs on Y-N phase to earth fault. As per DR at Muzaffarnagar end, fault current was ~2.43kA; fault sensed in zone-1 at Muzaffarnagar end.iii)As reported, at 12:47 hrs, 400 KV Alaknanda GVK(UPC)- Muzaffarnagar (UP) Ckt tripped on Y-N phase to earth fault followed by 3-phase fault. As per DR at Muzaffarnagar end, A/R was successful on Y-N fault (Iy=~2.36kA) from Muzaffarnagar end. Fault current for 3-ph fault from Muzaffarnagar end were Ir=~3.38kA, Iy=~2.67kA, Ib=~2.74kA. Y-N fault sensed in zone-2 (+carrier received) and 3-phase fault sensed in zone-4 at Muzaffarnagar end. As per DR at Alaknanda end, fault current for 3-ph fault from Alaknanda end were Ir=~2.28kA, Iy=~2.22kA, Ib=~2.26kA. Line tripped from Alaknanda end after sensing 3-phase fault in zone-1.iv)During the same time, 4 | grid_india_gd/grid_events/2026-05-01
G00271 | 2026-05 | 20 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-05-19T01:06 | 2026-05-19T02:48 | 1.7 | 80 | 340 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 80 MW occurred at Sewa-2(NH). | 20 GD-1 Jammu and Kashmir 19-05-2026 01:06 19-05-2026 02:48 01:42 80 340 13.90% 43.34% 57557 78455 i)220/132kV Hiranagar(JK) has double main Bus arrangement at both 220kV and 132kV level. ii)During antecedent condition, 40 MW Sewa-II HPS - UNIT 1 & 2 were in running condition and generating approx 40 MW each (as per SCADA). iii)As reported, at 01:06hrs, R-ph CT blast occurred at LV side of 220/132kV 120 MVA ICT-2 at Hiranagar(JK) which led to delayed fault clerance. iv)Due to this, all 220kV elements connected to both the buses of 220kV Hiranagar(JK) tripped (exact nature of protection operated in 220kV lines and 220/132kV ICTs yet to be shared) and complete blackout occurred at 220/132kV Hiranagar(JK). 220 KV Samba(PG)-Hiranagar(PDD) (PDD JK) Ckt-2 tripped from Hiranagar end only.v)During the same time, 132kV feeders from Sewa-2(NH) to Hiranagar, Mahanpur and Kathua also tripped (exact reason of tripping yet to be shared) which led to tripping of all running units at Sewa-2(NH) due to loss of evacuation path. Hence complete blackout occurred at 132kV Sewa-2(NH).vi)As per PMU at Sambha(PG), R-N phase to earth with delayed fault clearing time of 1040 ms was observed.vii)As per SCADA, change in demand of approx 340 MW was observed in J&K control area. Generation loss of approx 80 MW occurred at Sewa-2(NH). 1) 220 KV Samba(PG)-Hiranagar(PDD) (PG) Ckt-1 2) 220 KV Samba(PG)-Hiranagar(PDD) (PDD JK) Ckt-2 3) 220/132kV 200 MVA ICT-1 at Hiranagar(JK) 4) 220/132kV 120 MVA ICT-2 at Hira | grid_india_gd/grid_events/2026-05-01
G00272 | 2026-05 | 72 | GI-2 | Telangana | TG | Southern | 2026-05-19T19:02 | 2026-05-19T22:11 | 3.15 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | This led to the Tripping of 400kV and 220kV Bus-1 at Gajwel of TGTRANSCO 400KV/220KV GAJWEL-ICT-1, 400KV/220KV GAJWEL-ICT-2, 400KV-GAJWEL-RAMAGUNDAM-1, 400KV-GHANAPUR- GAJWEL-1 Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 1 GI-2 TELANGANA 19-05-2026 19:02 19-05-2026 22:11 03:09 0 0 0.00% 0.00% 52073.7 54825.85 Tripping of 400kV Bus-1 of 400kV Shankarapally SS of TGTRANSCO As per the reports submitted, the triggering incident was Y-G fault in 400kV Kethyreddypalli Shankarapally line-1. During which, even after the breaker opening at Shankarapally end, due to DC current component, the current persisted to flow in the line and LBB sensed the breaker did not open and LBB operated after around 200ms tripping all the main breakers connected to 400kV Bus-1 of 400kV Shankarapally SS. Due to PSL logic issue 400KV-NIZAMABAD-SHANKARAPALLY-1&2 also tripped during the event. This led to the Tripping of 400kV Bus-1 of 400kV Shankarapally SS of TGTRANSCO. 400KV-NIZAMABAD-SHANKARAPALLY-2, 400KV-NIZAMABAD- SHANKARAPALLY-1, 400KV-KETHIREDDYPALLY- SHANKARAPALLY-1, SHANKARAPALLY - 400KV - Bus 1 GI-1 ANDHRA PRADESH 22-05-2026 07:38 22-05-2026 11:43 04:05 0.0 0.0 0.00% 0.00% 49686.11 51184.18 Tripping of 220kV Bus-2 of 220kV Gooty SWS of APTRANSCO 220kV Gooty SWS is operating with double bus with bus coupler configuration. As per the reports submitted, the triggering incident was R-G fault in 220kV Gooty Bus- 2. Immedeately, 220kV Bus-2 BBP operated and all elements connected to the bus trpped leading to loss of power supply to 220kV Bus-2 of 220kV Gooty SWS GOOTY-SWS - 220KV - Bus 2, 220KV-GOOTY-SWS-DHONE-2, 220KV-GOOTY-SWS-GOOTY-RLY-1, 400KV/220KV GOOTY-ICT- 1, 400KV/220KV GOOTY-ICT-2, 220KV-GOOTY-SWS- SHAPURAM-1 | grid_india_gd/grid_events/2026-05-01
G00273 | 2026-05 | 22 | GD-1 | Haryana | HR | Northern | 2026-05-20T09:33 | 2026-05-20T09:50 | 0.28 | 0 | 650 | FALSE | FALSE | FALSE | FALSE | FALSE | 22 GD-1 Haryana 20-05-2026 09:33 20-05-2026 09:50 00:17 0 650 0.00% 83.56% 71974 77792 i) 220kV Sec72 Gurgaon (HR) receives supply from 400/220kV Gurgaon (PG) through three 220kV feeders and the 220kV Sec72–Sec69 Gurgaon circuit. Sec69 Gurgaon is connected to 400/220kV Sohna Road (GPTL). Sec72 suppl | 22 GD-1 Haryana 20-05-2026 09:33 20-05-2026 09:50 00:17 0 650 0.00% 83.56% 71974 77792 i) 220kV Sec72 Gurgaon (HR) receives supply from 400/220kV Gurgaon (PG) through three 220kV feeders and the 220kV Sec72–Sec69 Gurgaon circuit. Sec69 Gurgaon is connected to 400/220kV Sohna Road (GPTL). Sec72 supplies power to 220/66kV Sec56, Sec52, Sec57, and Sec20 Gurgaon substations. Rapid Metro is fed from 220/66kV Sec56 Gurgaon via a single-circuit 66kV line. DMRC Yellow Line is connected to 220/66kV Sec52 Gurgaon through a double-circuit 66kV line to HUDA City Centre and has alternate supply from the DTL network via 220/66kV Mehrauli (DTL)–Chattarpur. ii) At 09:38 hrs, the R-phase CT of 220kV Gurgaon (PG)–Sec72 Gurgaon ckt-I at Sec72 end was damaged and caught fire. Consequently, Bus-II busbar protection at Sec72 and line differential protection at Gurgaon (PG) operated, tripping ckt-I and all elements connected to 220kV Bus-II at Sec72.iii) About 1.4 seconds later, the damaged R-phase CT caused a fault on 220kV Bus-I at Sec72. Bus-I busbar protection operated, tripping all elements connected to Bus-I. As per DR, Busbar Zone-2 protection operated on an R-N fault at 09:33:55 hrs, followed by Busbar Zone-1 protection on a Y-B fault at 09:33:56 hrs.iv) PMU data at Gurgaon (PG) indicates an R-N fault followed by a Y-B fault, both cleared within 100 ms.v) As per DR at Gurgaon (PG), Line-I tripped on R-phase differential protection at 09:33:55 hrs. Line-II detected the Y-B fault as a through | grid_india_gd/grid_events/2026-05-01
G00274 | 2026-05 | 23 | GI-2 | Haryana | HR | Northern | 2026-05-20T12:33 | 2026-05-20T14:15 | 1.7 | 0 | 100 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 800 KV HVDC Kurukshetra(PG) Pole-3 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. | 23 GI-2 Haryana 20-05-2026 12:33 20-05-2026 14:15 01:42 0 100 0.00% 12.43% 68841 80446 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~4500 MW power from Champa to Kurukshetra (~1500 MW on Pole-2, 3, & 4; Pole-1 was already in tripped condition) (as per SCADA). ii)Power ramp-up code received to increase power from 3000MW to 4500MW. Initial system voltage was 400KV and during ramp- up, system voltage decreased to 387 KV and pole-3 converter transformer taps raised to 30 to achieve desired Valve Winding voltage i.e., 334 kV. After ramp up D-type filters manually switched in to maintain AC side voltage around 400KV.iii)However, actual Valve Winding voltage was around 352kV which has surpassed the protection set level of Inhibit Tap Up alarm and alarm appeared multiple times. As “Inhibit Tap Up” is Minor fail alarm so pole-3 control attempted lane-changeover multiple times.iv)Valve Winding voltage in pole-3 control initiated “Force Tap Down” to maintain the voltage, however the voltage remain high around 368KV. and Valve winding Overvoltage protection latched in L1M1 of pole-3 as voltage crossed its set level (i.e., 1.067 pu for 60 sec).v)As “Inhibit Tap Up” alarm present in Active & Standby lane and Overvoltage appeared in one protection of Active Lane, lane changeover could not happen in this case and Pole-3 got blocked at 12:32:36.980 hrs.vi)Further, at 12:33:36.760 hrs, Pole-4 got blocked due to the latching of Valve Winding Overvoltage protec | grid_india_gd/grid_events/2026-05-01
G00275 | 2026-05 | 21 | GI-2 | Delhi | DL | Northern | 2026-05-20T13:57 | 2026-05-20T15:19 | 1.37 | 0 | 480 | FALSE | FALSE | FALSE | FALSE | FALSE | 21 GI-2 Delhi 20-05-2026 13:57 20-05-2026 15:19 01:22 0 480 0.00% 59.20% 73153 81087 i)400/220KV Bamnauli(DTL) has double main and double breaker bus scheme in 400KV and double main & transfer bus system in 220KV voltage level. The 220KV system is divided into 2 sections consisting of 220KV Bus-A, 2 | 21 GI-2 Delhi 20-05-2026 13:57 20-05-2026 15:19 01:22 0 480 0.00% 59.20% 73153 81087 i)400/220KV Bamnauli(DTL) has double main and double breaker bus scheme in 400KV and double main & transfer bus system in 220KV voltage level. The 220KV system is divided into 2 sections consisting of 220KV Bus-A, 220KV Bus-B, 220KV Bus-C and 220KV Bus-D connected by 220KV Bus Sectionalizers. ii)During antecedent condition, 400/220 KV 500 MVA ICT 2 & 3 were carrying 236 MW and 239 MW respectively and were running in parallel and feeding the load of 220kV Dial, Papankalan-II (Part load), Najafgarh S/Stn. (Part load). iii)As reported, at 13:57 hrs, 220KV Bamnauli- Najafgarh (DTL) Ckt-1 tripped on R-Y phase to phase fault with fault distance of 5.2km from Najafgarh end due to jumper snapping near Najafgarh end and fault sensed in zone-1 at both the ends. iv)220KV Bamnauli- Najafgarh (DTL) Ckt-2 also tripped on Y-N phase to earth fault and fault sensed in zone-1 at Najafgarh end and differential protection operated, as further reported (exact reason, nature and location of fault yet to be shared). v)During the same time, 400/220 kV 500 MVA ICT 2 & 3 at Bamnoli(DTL) also tripped (exact reason and nature of protection operation yet to be shared). vi)As per PMU at Agra(PG), R-Y phase to phase fault followed by Y-N phase to earth fault was observed with fault clearing time of 80 ms and 920 ms (delayed) respectively. vii)As per SCADA, change in demand of approx 450 MW was observed in Delhi control are | grid_india_gd/grid_events/2026-05-01
G00276 | 2026-05 | 65 | GI-1 | Chhattisgarh | CG | Western | 2026-05-20T21:58 | 2026-05-20T22:40 | 0.7 | 500 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 19 GI-1 Chhattisgarh 20-05-2026 21:58 20-05-2026 22:40 00:42 500 - 0.56% - 89841 72714 Partially outage of 220 kV Bishrampur and Churri: At 21:58 hrs /20-05-2026, the B-phase wave trap of the 132 kV Churri–Gevra Line-2 along with the Y-phase CT of ICT at the Gevra end burst. Due to the sudden electr | 19 GI-1 Chhattisgarh 20-05-2026 21:58 20-05-2026 22:40 00:42 500 - 0.56% - 89841 72714 Partially outage of 220 kV Bishrampur and Churri: At 21:58 hrs /20-05-2026, the B-phase wave trap of the 132 kV Churri–Gevra Line-2 along with the Y-phase CT of ICT at the Gevra end burst. Due to the sudden electrical/mechanical jerk caused by this failure, ICT-1 & ICT-2 (160 MVA each) at 220 kV Churri S/s and ICT-1 & ICT-2 (160 MVA each) at 220 kV Bishrampur S/s tripped. Consequently, supply to 11 nos. of 132 kV substations (as mentioned in Table-9) and the connected 132 kV feeders at 220 kV Churri and Bishrampur substations was interrupted, as these substations are radially connected and became de-energized due to loss of supply. 1. 220 KV S/s Churri ICT-1, 2 3. 220 KV S/s Bishrampur ICT-1, 2 5. 132 kV / 33kV Chhurikhurd S/s 6. 132 kV / 33kV Bango 7. 132 kV / 33kV Manendragarh 8. 132 kV / 33kV Ambikapur 9. 132 kV / 33kV Gevra (SECL) 10. 132 kV / 33kV Baikunthpur 11. 132 kV / 33kV Pratappur 12. 132 kV / 33kV Wadrafnagar 13. 132 kV / 33kV Udaypur 14. 132 kV / 33kV Rajpur 15. 132 kV / 33kV Balrampur | grid_india_gd/grid_events/2026-05-01
G00277 | 2026-05 | 24 | GI-1 | Haryana | HR | Northern | 2026-05-21T20:52 | 2026-05-21T23:45 | 2.88 | 0 | 275 | FALSE | FALSE | FALSE | FALSE | FALSE | 24 GI-1 Haryana 21-05-2026 20:52 21-05-2026 23:45 02:53 0 275 0.00% 34.59% 62560 79509 i)220KV Hissar IA(HVPNL) Sub-station has double main bus system. ii)As reported, at 20:52hrs, R-phase CT of 220 KV Hissar(BB)-Hissar IA(HV) (HVPNL) Ckt-1 at Hissar IA end got damaged creating bus fault. Line tripp | 24 GI-1 Haryana 21-05-2026 20:52 21-05-2026 23:45 02:53 0 275 0.00% 34.59% 62560 79509 i)220KV Hissar IA(HVPNL) Sub-station has double main bus system. ii)As reported, at 20:52hrs, R-phase CT of 220 KV Hissar(BB)-Hissar IA(HV) (HVPNL) Ckt-1 at Hissar IA end got damaged creating bus fault. Line tripped on R-N phase to earth fault with fault current of 31.12 kA from Hissar IA end. iii)During the same time, busbar protection also operated at Hissar IA(HV) end and 220 KV Hissar(BB)-Hissar IA(HV) (BBMB) Ckt-2 and 220 KV Hissar(PG)-Hissar IA(HV) (PG) Ckt- 1 & 2 also tripped (bus-wise arrangement of elements at 220kV Hissar IA yet to be shared). iv)As per SCADA SOE, 220kV Hissar IA-Narwana (HVPNL) Ckt and 220kV Hissar IA-Masudpur (HVPNL) Ckt-1 also tripped during the same time (exact reason of tripping yet to be shared). v)As per PMU at Hissar(PG), R-N phase to earth fault with fault clearing time of 120 ms is observed. vi)As per SCADA, change in demand of approx 275 MW was observed in Haryana control area. 1) 220 KV Hissar(BB)-Hissar IA(HV) (BBMB) Ckt-2 2) 220 KV Hissar(BB)-Hissar IA(HV) (HVPNL) Ckt-1 3) 220 KV Hissar(PG)-Hissar IA(HV) (PG) Ckt-2 4) 220 KV Hissar(PG)-Hissar IA(HV) (PG) Ckt-1 | grid_india_gd/grid_events/2026-05-01
G00278 | 2026-05 | 26 | GD-1 | Haryana | HR | Northern | 2026-05-22T19:37 | 2026-05-22T22:11 | 2.57 | 0 | 10 | FALSE | FALSE | FALSE | FALSE | FALSE | 26 GD-1 Haryana 22-05-2026 19:37 22-05-2026 22:11 02:34 0 10 0.00% 1.26% 60582 79118 i)220/132kV Jagadhari Railways has connectivity from 400/220kV Abdullapur(PG) through 220kV D/C. During antecedent condition, 220 KV Abdullapur(PG)-New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-1 & 2 were carrying approx | 26 GD-1 Haryana 22-05-2026 19:37 22-05-2026 22:11 02:34 0 10 0.00% 1.26% 60582 79118 i)220/132kV Jagadhari Railways has connectivity from 400/220kV Abdullapur(PG) through 220kV D/C. During antecedent condition, 220 KV Abdullapur(PG)-New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-1 & 2 were carrying approx 10 MW and 0 MW respectively (as per SCADA). ii)As reported, at 19:37hrs, R-phase PT of the 220 KV Abdullapur(PG)- New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-1 burst at Jagadhari. Immediately thereafter, the B-phase PT of the 220 KV Abdullapur(PG)-New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-2 also burst resulting in the tripping of both 220 kV circuits. iii)Due to tripping of both the circuits, complete blackout occurred at 220/132kV Jagadhari Railways. Consequently, the railway power supply between Sambhu and Hapur was affected. iv)As per telephonic conversation, it was informed that the railway supply was restored from Khanna(PS) at 21:15 hrs. v)As per PMU at Abdullapur(PG), R-N phase to earth fault followed by B-N phase to earth fault with delayed fault clearing time of 200 ms was observed. vi)As per SCADA, no change in demand was observed in Haryana control area. As per Jagadhari Railways, load loss of approx 10 MW occurred. 1) 220 KV Abdullapur(PG)-New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-1 2) 220 KV Abdullapur(PG)-New Jagadhari TSS(DFCCIL) (RAILWAYS) Ckt-2 | grid_india_gd/grid_events/2026-05-01
G00279 | 2026-05 | 25 | GD-1 | Haryana | HR | Northern | 2026-05-22T19:50 | 2026-05-22T20:05 | 0.25 | 0 | 932 | FALSE | FALSE | FALSE | FALSE | FALSE | 25 GD-1 Haryana 22-05-2026 19:50 22-05-2026 20:05 00:15 0 932 0.00% 116.43% 60430 80048 i) 220kV Sec-72 Gurgaon (HR) receives supply from 400/220kV Gurgaon (PG) through three 220kV feeders and the 220kV Sec72–Sec69 Gurgaon circuit. Sec69 Gurgaon is connected to 400/220kV Sohna Road (GPTL). Sec72 sup | 25 GD-1 Haryana 22-05-2026 19:50 22-05-2026 20:05 00:15 0 932 0.00% 116.43% 60430 80048 i) 220kV Sec-72 Gurgaon (HR) receives supply from 400/220kV Gurgaon (PG) through three 220kV feeders and the 220kV Sec72–Sec69 Gurgaon circuit. Sec69 Gurgaon is connected to 400/220kV Sohna Road (GPTL). Sec72 supplies 220/66kV Sec56, Sec52, Sec57, and Sec20 Gurgaon substations. Rapid Metro receives power from 220/66kV Sec56 Gurgaon via a single-circuit 66kV line. DMRC Yellow Line is connected to 220/66kV Sec52 Gurgaon through a double-circuit 66kV line to HUDA City Centre and also has alternate supply from the DTL network through 220/66kV Mehrauli (DTL)–Chattarpur.ii) At 19:50 hrs, the R-phase CT of 220kV Gurgaon (PG)–Sec72 Gurgaon ckt-I at Sec72 end was damaged and caught fire. Busbar protection of 220kV Bus-II at Sec72 and line differential protection at Gurgaon (PG) operated, tripping ckt-I while other 220kV elements remained in service. After ~300 ms, the R-phase jumper of Line-III snapped from the CT/isolator clamp, the Y-phase jumper of Line-I snapped from CB to CT, and the R-phase jumper of the bus coupler snapped from the Bus-II isolator. These faults again operated the busbar protection, which tripped all 220kV elements due to bus-tie condition caused by incorrect isolator status. As per DR, fault clearance was delayed by ~400 ms.iii) PMU data at Gurgaon (PG) shows an R-N fault, followed by R-N and B-N faults, which evolved into an R-Y fault with delayed clearance of ~480 msiv) As | grid_india_gd/grid_events/2026-05-01
G00280 | 2026-05 | 27 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-22T22:48 | 2026-05-22T23:33 | 0.75 | 81 | 108 | FALSE | FALSE | FALSE | FALSE | FALSE | However, as reported by SLDC UP, load loss of 108 MW in UP control area and generation loss of 81 MW at Bajaj Energy Maqsoodpur occurred. | 27 GD-1 Uttar Pradesh 22-05-2026 22:48 22-05-2026 23:33 00:45 81 108 12.75% 13.00% 63525 83078 i)220/132kV Shahjahanpur(UP) has double main and transfer bus scheme at 220kV level and single main and transfer bus scheme at 132kV level. ii)During antecedent condition, 45 MW Bajaj Energy Maqsoodpur Unit-1 & 2 were generating approx 40 MW and 41 MW respectively (as per SCADA). iii)As reported, at 22:48 hrs, 220kV R-ph CT of Bus coupler blast occurred at Shahjahanpur (UP). Y-ph jumper of jack bus (bus coupler) came into range of B-ph of Bus-1 as suspension string was damaged. iv)Bus-bar relay at 220kV Shahjahanpur(UP) was in lockout condition and hence relay did not operate. Isolator ON/OFF status was also not as per site condition of isolator. v)Hence, all 220kV lines tripped from remote ends sensing the fault in zone-2 except 220 KV Shahjahanpur(PG)-Shahjahanpur(UP) (UP) Ckt. As per DR at Shahjahanpur(PG) end, B-N fault (Ib=~7.69kA) immediately followed by Y-N fault (Iy=~7.93kA) was observed and zone-1 operated at Shahjahanpur(PG) end. vi)Due to tripping of all the elements connected to both Bus-1 and 2, complete blackout occurred at 220/132kV Shahjahanpur(UP) S/s. vii)45 MW Bajaj Energy Maqsoodpur Unit-1 & 2 also tripped during the same time due to loss of evacuation path.viii)As per PMU at Bareilly(PG), B-N Phase to earth fault converted to Y-B-N double phase to earth was observed with delayed fault clearance time of 280 ms. ix)As per SCADA, change in demand of approx 304 MW i | grid_india_gd/grid_events/2026-05-01
G00281 | 2026-05 | 28 | GD-1 | Haryana | HR | Northern | 2026-05-23T00:12 | 2026-05-23T01:58 | 1.77 | 0 | 150 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-1 2) 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. | 28 GD-1 Haryana 23-05-2026 00:12 23-05-2026 01:58 01:46 0 150 0.00% 18.46% 62215 81255 i)220/132KV Samalkha(HVPNL) Sub-station has double main bus system at both 220kV and 132kV level. ii)During antecedent condition, 220kV Chajpur-Samalkha(HV) Ckt-1 & 2 were already under outage. 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-1 & 2 were carrying 69 MW and 73 MW respectively (as per SCADA). iii)As reported, at 00:12hrs, Y-ph CT of 220/132kV 100 MVA ICT-6 at Samalkha(HV) got damaged. iv)During the same time, 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-1 & 2 also tripped (exact nature of protection operated yet to be shared). v)Due to tripping of both 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-1 & 2, complete blackout occurred at 220/132KV Samalkha(HV). vi)As per PMU at Sonipat(PG), Y-N phase to earth fault followed by Y-B-N double phase to earth fault with fault clearing time of 80 ms and 480 ms respectively was observed. vii)As per SCADA, change in demand of approx 215 MW was observed in Haryana control area. However, as reported by SLDC Haryana, load loss of approx 150 MW occurred. 1) 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-1 2) 220 KV Sonipat(PG)-Samalkha(HV) (HVPNL) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occur | grid_india_gd/grid_events/2026-05-01
G00282 | 2026-05 | 66 | GD-1 | Maharashtra | MH | Western | 2026-05-23T18:02 | 2026-05-23T23:35 | 5.55 | 37 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 25 MW occurred at , 400kV Tuljapur due to the loss of evacuation path. | 20 GD-1 Maharashtra 23-05-2026 18:02 23-05-2026 23:35 05:33 37 - 0.04% - 87646 73079 Complete outage of 400 kV Tuljapur (Renew Green PSS1 Wind): At 18:02 hrs/23-05-2026, the 400 kV Tuljapur PSS-1–Konhali PSS-4 line tripped on an R-phase to earth fault under conditions of heavy wind and intense lightning. Generation loss of 25 MW occurred at , 400kV Tuljapur due to the loss of evacuation path. 1. 400 kV Tuljapur PSS-1-Konhali PSS-4 2. 400kV Tuljapur Bus 1 3. 400kV Tuljapur Bus 2 4. 400/33 kV Tuljapur PSS-1 ICT | grid_india_gd/grid_events/2026-05-01
G00283 | 2026-05 | 67 | GD-1 | Maharashtra | MH | Western | 2026-05-23T19:06 | 2026-05-23T21:57 | 2.85 | 42 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 72MW reported by the plant. | 21 GD-1 Maharashtra 23-05-2026 19:06 23-05-2026 21:57 02:51 42 - 0.05% - 87720 73035 Complete outage of 220 kV Tandulwadi (Serentica): At 19:06 Hrs/23-05-2026, 220 kV Tandulwadi- Kallam line tripped at Tandulwadi end only on 86 & 96 Relay operation. Due to the loss of evacuation path, 220 kV Tandulwadi Wind Power Plant went dark. Generation loss of 72MW reported by the plant. 1. 220 kV Tandulwadi - Kallam-1 | grid_india_gd/grid_events/2026-05-01
G00284 | 2026-05 | 76 | GD-1 | Odisha | OD | Eastern | 2026-05-23T21:54 | 2026-05-23T23:02 | 1.13 | 0 | 300 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GD-1 Odisha 23-05-2026 21:54 23-05-2026 23:02 01:08 0 300 0.00% 0.93% 37120 32086 Prior to the disturbance 220 kV Bolangir (GRIDCO)- Bargarh and 220kV Bolangir (GRIDCO)- Kesinga line was idle-charged on system requirements and Bolangir(GRIDCO) was connected through 220kV Bolangir(GRIDCO)-Bolangir( | 4 GD-1 Odisha 23-05-2026 21:54 23-05-2026 23:02 01:08 0 300 0.00% 0.93% 37120 32086 Prior to the disturbance 220 kV Bolangir (GRIDCO)- Bargarh and 220kV Bolangir (GRIDCO)- Kesinga line was idle-charged on system requirements and Bolangir(GRIDCO) was connected through 220kV Bolangir(GRIDCO)-Bolangir(PG) D/C line. At 21:54 Hrs, R-phase CVT of 132KV Bolangir(GRIDCO)- Patnagarh got burst which created R- Earth fault which was cleared from remote end in Z-3 protection by tripping of 220kV Bolangir(GRIDCO)-Bolangir(PG) D/C from Bolangir(PG) end. 220kV Bolangir(GRIDCO) S/s became dead. Total load loss of 300 MW was reported at Bolangir(GRIDCO) S/s. 220 kV Bolangir (PG)-Bolangir (GRIDCO) -1 220 kV Bolangir (PG)-Bolangir (GRIDCO) -2 | grid_india_gd/grid_events/2026-05-01
G00285 | 2026-05 | 68 | GD-1 | Maharashtra | MH | Western | 2026-05-24T02:34 | 2026-05-24T04:06 | 1.53 | 30 |  | FALSE | TRUE | FALSE | FALSE | TRUE | 22 GD-1 Maharashtra 24-05-2026 02:34 24-05-2026 04:06 01:32 30 - 0.04% - 70660 86232 Complete outage of 220 kV Tandulwadi (Serentica): At 02:34 hrs on 24-05-2026, 220 kV Tandulwadi- Kallam line tripped on overcurrent protection (50) in the R, Y, and B phases, tripping is due to adverse weather conditions involving heavy wind and lightning, Subsequently, the 220 kV Busbar Protection (Relay 96) also | 22 GD-1 Maharashtra 24-05-2026 02:34 24-05-2026 04:06 01:32 30 - 0.04% - 70660 86232 Complete outage of 220 kV Tandulwadi (Serentica): At 02:34 hrs on 24-05-2026, 220 kV Tandulwadi- Kallam line tripped on overcurrent protection (50) in the R, Y, and B phases, tripping is due to adverse weather conditions involving heavy wind and lightning, Subsequently, the 220 kV Busbar Protection (Relay 96) also operated. The faulty 33 kV Feeder-02 was isolated from the system. 1. 220 kV Tandulwadi - Kallam-1 | grid_india_gd/grid_events/2026-05-01
G00286 | 2026-05 | 29 | GD-1 | Haryana | HR | Northern | 2026-05-24T04:10 | 2026-05-24T04:30 | 0.33 | 0 | 127 | FALSE | FALSE | FALSE | FALSE | FALSE | 29 GD-1 Haryana 24-05-2026 04:10 24-05-2026 04:30 00:20 0 127 0.00% 16.57% 54573 76633 i)220/66KV Shahbad(HVPNL) Sub-station has double main bus system at both 220kV and 66kV level. ii)As reported, at 04:10hrs, 220KV B-Ph LA,CT & CB limb of 220/66kV ICT-1 at Shahbad(HV) got damaged. iii)During the s | 29 GD-1 Haryana 24-05-2026 04:10 24-05-2026 04:30 00:20 0 127 0.00% 16.57% 54573 76633 i)220/66KV Shahbad(HVPNL) Sub-station has double main bus system at both 220kV and 66kV level. ii)As reported, at 04:10hrs, 220KV B-Ph LA,CT & CB limb of 220/66kV ICT-1 at Shahbad(HV) got damaged. iii)During the same time, all 220kV lines connected to Shahbad(HV) also tripped sensing the fault in zone-4 from Shahbad end only (exact nature and location of fault yet to be shared). iv)Due to this, complete blackout occurred at 220/66KV Shahbad(HV). v)As per PMU at Abdullapur(PG), B-N phase to earth fault followed by Y-B-N double phase to earth fault with fault clearing time of 80 ms and 400 ms respectively was observed. vi)As per SCADA, change in demand of approx 127 MW was observed in Haryana control area. 1) 220kV Shahbad-Jorian (HVPNL) Ckt-1 2) 220kV Shahbad-Jorian (HVPNL) Ckt-2 3) 220kV Shahbad-Durala (HVPNL) Ckt-1 4) 220kV Shahbad-Durala (HVPNL) Ckt-2 5) 220kV Shahbad-Rajokheri (HVPNL) Ckt-1 6) 220kV Shahbad-Rajokheri (HVPNL) Ckt-2 | grid_india_gd/grid_events/2026-05-01
G00287 | 2026-05 | 30 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-24T04:45 | 2026-05-24T05:15 | 0.5 | 0 | 140 | FALSE | FALSE | FALSE | FALSE | FALSE | 30 GD-1 Uttar Pradesh 24-05-2026 04:45 24-05-2026 05:15 00:30 0 140 0.00% 18.28% 55023 76592 i)220/132kV Shamsabad(UP) has single main and transfer bus scheme at both 220kV and 132kV level. ii)As reported, at 04:45 hrs, R-ph CT of 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt at Shamsabad (UP) end got burs | 30 GD-1 Uttar Pradesh 24-05-2026 04:45 24-05-2026 05:15 00:30 0 140 0.00% 18.28% 55023 76592 i)220/132kV Shamsabad(UP) has single main and transfer bus scheme at both 220kV and 132kV level. ii)As reported, at 04:45 hrs, R-ph CT of 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt at Shamsabad (UP) end got burst. iii)As per DR, bus-bar relay at 220kV Shamsabad(UP) picked up and zone-1 differential trip operated. iv)As per DR of Agra(UP) end of 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt, R-N fault (Ir=~4.98kA) followed by R-Y fault (Ir=Iy=~6.21kA) was observed; fault sensed in zone-2 at Agra(UP) end; fault clearing time was 320ms and 400ms respectively. v)Due to tripping of all 220kV lines connected to 220kV bus at Shamsabad(UP), complete blackout occurred at 220/132kV Shamsabad(UP) S/s. vi)As per PMU at Agra(PG), R-N Phase to earth fault followed by R-Y phase to phase fault was observed with delayed fault clearance time of 320 ms and 400 ms respectively. vii)As per SCADA, change in demand of approx 137 MW in UƩar Pradesh control area was observed. As reported by SLDC UP , load loss of 140 MW occurred in UP control area. 1) 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt 2) 220 KV Agra(PG)-Shamsabad(UP) (UP) Ckt 3) 220/132kV 160 MVA ICT-1 at Shamsabad(UP) 4) 220/132kV 160 MVA ICT-2 at Shamsabad(UP) | grid_india_gd/grid_events/2026-05-01
G00288 | 2026-05 | 31 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-24T12:20 | 2026-05-24T12:34 | 0.23 | 0 | 133 | FALSE | FALSE | FALSE | FALSE | FALSE | 31 GD-1 Uttar Pradesh 24-05-2026 12:20 24-05-2026 12:34 00:14 0 133 0.00% 18.11% 63851 73440 i)220/132kV Shamsabad(UP) has single main and transfer bus scheme at both 220kV and 132kV level. ii)As reported, at 12:20 hrs, Busbar protection operated during testing of R-ph CT of 220 KV Agra(UP)-Shamsaba | 31 GD-1 Uttar Pradesh 24-05-2026 12:20 24-05-2026 12:34 00:14 0 133 0.00% 18.11% 63851 73440 i)220/132kV Shamsabad(UP) has single main and transfer bus scheme at both 220kV and 132kV level. ii)As reported, at 12:20 hrs, Busbar protection operated during testing of R-ph CT of 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt at 220kV Shamsabad(UP). During investigation, metering core was found shorted to bus bar core of CT which was not directly visible. iii)As per DR, bus-bar relay gave tripping command on breaker failure as it sensed current of ~141 A flowing through Bay-4 (220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt) even though its CB was open. As per DR of Agra(UP) end of 220 KV Agra(UP)-Shamsabad(UP) (UP) Ckt, only R-ph current magnitude was 96 A. iv)Due to bus bar protection operation and tripping of all 220kV lines connected to 220kV bus at Shamsabad(UP), complete blackout occurred at 220/132kV Shamsabad(UP) S/s. v)As per PMU at Agra(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 133 MW in UƩar Pradesh control area was observed. As reported by SLDC UP , load loss of 133 MW occurred in UP control area. 1) 220 KV Agra(PG)-Shamsabad(UP) (UP) Ckt 2) 220/132kV 160 MVA ICT-1 at Shamsabad(UP) 3) 220/132kV 160 MVA ICT-2 at Shamsabad(UP) | grid_india_gd/grid_events/2026-05-01
G00289 | 2026-05 | 33 | GD-1 | Rajasthan | RJ | Northern | 2026-05-25T11:39 | 2026-05-25T11:44 | 0.08 | 0 | 180 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Neemrana(PG)-Kushkhera (RS) (RS) Ckt 2) 220 KV Bhiwadi(PG)-Kushkhera (RS) (RS) Ckt 3) 220 KV Karoli(RS)-Kushkhera (RS) (RS) Ckt 4) 220 KV KG Bass(RS)-Kushkhera (RS) (RS) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month o | 33 GD-1 Rajasthan 25-05-2026 11:39 25-05-2026 11:44 00:05 0 180 0.00% 21.89% 72670 82215 i)220kV Kushkhera(RS) has double main bus scheme. ii)During antecedent condition, 220kV Neemrana(PG)-Kushkhera(RS) (RS) Ckt and 220 KV Bhiwadi(PG)-Kushkhera(RS) (RS) Ckt were carrying 166 MW & 126 MW respectively. iii)As reported, at 11:39 hrs, R-ph jumper of 220kV Main Bus-II Isolator of at Kushkhera end of 220 KV Neemrana(PG)- Kushkhera (RS) (RS) Ckt got damaged and created bus fault. iv)As per DR, on this fault, bus bar protection operated (both Z-I and Z-II) at Kushkhera(RS) and leading to tripping of all the elements connected at 220kV Kushkhera(RS). (Reason of tripping of both the 220kV bus yet to be received). v)As per PMU at Bhiwadi(PG), R-N phase to earth fault was observed with fault clearing time of 80ms. vi)As per SCADA, change in demand of approx 180 MW in Rajasthan control area is observed. 1) 220 KV Neemrana(PG)-Kushkhera (RS) (RS) Ckt 2) 220 KV Bhiwadi(PG)-Kushkhera (RS) (RS) Ckt 3) 220 KV Karoli(RS)-Kushkhera (RS) (RS) Ckt 4) 220 KV KG Bass(RS)-Kushkhera (RS) (RS) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during | grid_india_gd/grid_events/2026-05-01
G00290 | 2026-05 | 32 | GI-2 | Uttar Pradesh | UP | Northern | 2026-05-25T18:44 | 2026-05-25T21:14 | 2.5 | 630 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of ~630 MW is observed due to trippig of 660MW Unit-1 at Ghatampur(UP). | 32 GI-2 Uttar Pradesh 25-05-2026 18:44 25-05-2026 21:14 02:30 630 0 107.38% 0.00% 58668 76924 i)765/400/132KV Ghatampur(UP) has one and half breaker scheme in 765KV, 400KV and double main bus scheme in 132KV. It comprises of 3 X 660MW of generation. Unit-3 and 400kV system at Ghatampur is yet to be commissioned. ii)During antecedent condition, 660MW GHATAMPUR TPS - UNIT 1 was generating 630 MW . 765 KV RAMPUR_PRSTL -GHATAMPUR_TPS (UP) CKT-1 was carrying 590 MW and 765kV Ghatampur_TPS(UP)-Agra Fatehabad(UP) line was carrying ~41 MW. iii)As reported, at 18:44 hrs, 765 KV RAMPUR_PRSTL -GHATAMPUR_TPS (UP) CKT-1 tripped due to Y-N phase to earth fault. As per DR of Ghatampur(UP) end, Y-N fault in Z-1 (169.9km) and 2.45kA fault current with unsuccessful A/R operation is observed. iv)As per PMU at Agra(PG), Y-N phase to earth fault with unsuccessful A/R operation and fault clearance time of 80 msec is observed. v)At the same time, GT of 660MW GHATAMPUR TPS - UNIT 1 sensed earth fault and Type C protection operated which initiated house load operation. Generation of Ghatampur Unit-1 back down to 30 MW. However, within 01 minute, due to high temperature, turbine of unit-1 tripped and generation of unit-1 lost. vi)As per SCADA, generation loss of ~630 MW is observed due to trippig of 660MW Unit-1 at Ghatampur(UP). 1) 765 KV RAMPUR_PRSTL -GHATAMPUR_TPS (UP) CKT-1 2) 765 KV Ghatampur_TPS(UP) - Bus 2 3) 660MW GHATAMPUR TPS - UNIT 1 | grid_india_gd/grid_events/2026-05-01
G00291 | 2026-05 | 34 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-25T22:00 | 2026-05-25T22:28 | 0.47 | 1058 | 250 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA and reported by SLDC-UP, generation loss of ~1058 MW is observed in UP control area due to tripping of 4*300MW Units at Rosa TPS(UP) and load loss of ~250 MW occurred in UP control area due to blackout of 400/220kV Badaun(UP). | 34 GD-1 Uttar Pradesh 25-05-2026 22:00 25-05-2026 22:28 00:28 1058 250 163.48% 30.13% 64719 82975 i)400/220KV Rosa TPS(UP) has double main bus scheme at both 400kV & 220kV level and 400/220KV Badaun(UP) has one and half breaker scheme at 400KV level & double main bus scheme at 220KV level. Rosa TPS has 4*300 MW thermal generating units. ii)During antecedent condition, there was inclement weather condition (thunderstorm / windstorm). All four units 3*300 MW at Rosa TPS were running and generating total ~1058 MW. 660MW GHATAMPUR TPS - UNIT 1 was generating 630 MW. iii)As reported, at 20:40 hrs, 400kV Sambhal(PRSTL)-Badaun(UP) line-1 & 2 tripped on R-N fault. Further at 21:54 hrs, 400kV Badaun-Rosa (UP) line-1, 400kV Badaun-Farrukhabad (UP) line-1 and 400kV Shahjhanpur(PG)-Rosa (UP) line-1 tripped on phase to earth fault. 220kV Badaun-Rosa (UP) line-1 & 2 tripped at 21:58 hrs and 21:59 hrs respectively on phase to earth fault. iv)Further at 22:00 hrs, 400kV Badaun-Rosa (UP) line-2, 220kV Badaun-Dataganj (UP) line-1&2, 220kV Shahjhanpur(PG)-Rosa (UP) line-1&2 and 400kV Shahjhanpur(PG)- Rosa (UP) line-2 tripped on faults in line. Exact line wise details of fault and their DR/EL yet to be received from UP. v)With the tripping of above lines, 300 MW Unit-1, 2, 3 & 4 at Rosa TPS(UP) tripped due to loss of evacuation path and both of 400/220kV Rosa TPS(UP) & Badaun(UP) became dead. vi)As per PMU at CB Ganj(UP) and Lucknow(PG), R-B fault at 21:54:14 hrs cleared within 100msec, R-Y-B fa | grid_india_gd/grid_events/2026-05-01
G00292 | 2026-05 | 77 | GD-1 | Bihar | BR | Eastern | 2026-05-25T23:15 | 2026-05-25T23:30 | 0.25 | 0 | 25 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 5 GD-1 Bihar 25-05-2026 23:15 25-05-2026 23:30 00:15 0 25 0.00% 0.08% 36315 30440 Prior to the disturbance 220kV Begusarai-Khagaria D/C was kept open on system requirement and due to inclement weather 220KV-SAHARSA(PMTL)-KHAGARIA(NEW)- 1 & 2 and 220KV-KHAGARIA-NEW PURNEA-1 tripped at 22:04 Hrs, 22:36 Hrs and 22:54 Hrs on 25/05/2026 in phase to ground fault. At this time Khagaria S/s was radially connected through 220kV Khagaria-New Purnea -2. At 23:15 Hrs on 25/05/2026, R-Y-B phase fault occurred in 220kV New Purnea-Khagaria-2 and line got tripped, resulting in 220kV Khagaria S/s became dead. Total load loss of 25 MW reported at Khagaria S/s. 220KV-SAHARSA(PMTL)-KHAGARIA(NEW)-1 220KV-SAHARSA(PMTL)-KHAGARIA(NEW)-2 220KV-KHAGARIA-NEW PURNEA-1 220KV-KHAGARIA-NEW PURNEA-2 Elements Tripped Details of Grid Events during the Month of May 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD I Manipur 01-05-2026 13:44 01-05-2026 15:00 01:16 0 20 0 | grid_india_gd/grid_events/2026-05-01
G00293 | 2026-05 | 35 | GI-2 | Delhi, Rajasthan |  |  | 2026-05-27T12:53 | 2026-05-27T17:18 | 4.42 | 2270 | 1124 | TRUE | FALSE | FALSE | FALSE | TRUE | x)As per SCADA, change in NR total solar generation of approx 2270 MW was observed. | 35 GI-2 Delhi, Rajasthan 27-05-2026 12:53 27-05-2026 17:18 04:25 2270 1124 322.01% 134.16% 70494 83782 i)400kV CCGT Bawana(PPCL) has one and half breaker scheme at 400kV level. ii)During antecedent condition, CCGT Bawana(PPCL) unit-1 & 2 and STG-1 were generating approx 145 MW, 152 MW and 184 MW respectively (as per SCADA). Unit-3 & 4 and STG-2 were not in service. iii)As reported, at 12:53 hrs, B-ph jumper of 400 KV Bawana CCGTB(DTL)- Bahadurgarh(PG) (PG) Ckt (Bay 413 at CCGT Bawana) snapped at CCGT Bawana. iv)As per DR at CCGT Bawana end of 400 KV Bawana CCGTB(DTL)-Bahadurgarh(PG) (PG) Ckt, B- N phase to earth fault was observed with fault current of 42.79kA from CCGT Bawana; fault sensed in zone-1 at CCGT Bawana. v)Since 400 KV Bawana CCGTB(DTL)-Bhiwani(PG) (PG) Ckt (Bay 415 at CCGT Bawana) was in same D of one and half breaker scheme with Bay 414 being the tie bay, the same fault was also sensed by 400 KV Bawana CCGTB(DTL)-Bhiwani(PG) (PG) Ckt. vi)As per DR at CCGT Bawana end of 400 KV Bawana CCGTB(DTL)-Bhiwani(PG) (PG) Ckt, TEED protection operated at CCGT Bawana end. Very high magnitude of through fault current resulted into pick up of High set element of TEED differential protection. vii)As per PMU at Abdullapur(PG), Y-N phase to earth fault followed by B-N phase to earth fault was observed with fault clearing time of 120 ms and 80 ms respectively. viii)As per SCADA, change in demand of approx 292 MW in Delhi control area and 832 MW in Punjab Control area were observed | grid_india_gd/grid_events/2026-05-01
G00294 | 2026-05 | 36 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-05-27T18:04 | 2026-05-27T19:38 | 1.57 | 446 | 765 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 446 MW occurred at Salal(NH). | 36 GD-1 Jammu and Kashmir 27-05-2026 18:04 27-05-2026 19:38 01:34 446 765 72.78% 96.56% 61277 79223 i)400/220kV Kishenpur(PG) S/s has one & half breaker bus scheme at 400kV level and double main & transfer bus scheme at 220kV level. ii)During antecedent condition, 220kV Kishenpur(PG)-Mirbazar(JK) Ckt and 115 MW Unit-3 at Salal(NH) were out of service. Total generation of Salal was ~446 MW. iii)As reported, at 18:04 hrs, both 220kV Bus-1 and 2 at Kishenpur(PG) tripped on Busbar differential (zone-1 & zone-2) protection operation (as per DR). As all the 220kV elements connected at Kishenpur(PG) tripped, both the 220kV buses became dead. iv)Upon switchyard inspection it was observed that R-ph CT of the 220 KV Kishenpur(PG)-Udhampur(PDD) (PG) Ckt-2 (on Bus-2) has failed. Further, fire and smoke from the failed CT resulted in external flashover and external damage in Y-ph CT of the same line and B-ph CT of the adjacent 220 KV Kishenpur(PG)-Udhampur(PDD) (PG) Ckt-1 (on Bus- 1). This led to fault in both the buses at 220kv Kishenpur(PG). v)During the same time, all the running units of Salal(NH) tripped due to loss of evacuation path and complete blackout occurred at 220kV Salal(NH). vi)As per PMU at Kishenpur(PG), R-N phase to earth fault immediately followed by Y-B phase to phase fault was observed with fault clearing time of 80 ms and 120 ms respectively. vii)As per SCADA, change in demand of approx 765 MW was observed in J&K control area. Generation loss of approx 446 MW occurre | grid_india_gd/grid_events/2026-05-01
G00295 | 2026-05 | 38 | GD-1 | Delhi | DL | Northern | 2026-05-28T10:57 | 2026-05-28T11:03 | 0.1 | 0 | 240 | FALSE | FALSE | FALSE | FALSE | FALSE | 220/66kV 100 MVA ICT-2 at Mehrauli (DTL) 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of May 2026 in Northern Region Elements Tripped SlNo. | 38 GD-1 Delhi 28-05-2026 10:57 28-05-2026 11:03 00:06 0 240 0.00% 30.88% 68641 77709 i)220/66kV Mehrauli(DTL) has double main Bus arrangement at 220kV side. ii)During antecedent condition, 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-2 and 220kV Bus-II at Mehrauli(DTL) were under planned shutdown for maintenance purpose. 220kV Mehrauli-DIAL D/C and 220kV Mehrauli-Vasant Kunj D/C were in open condition from DIAL and Vasant Kunj end respectively for load management. 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 was the only source for load of Mehrauli at 66kV level and its MW loading was ~240 MW. iii)As reported, at 10:55 hrs, during switching of bus isolators for restoring of 220kV Bus-2 at Mehrauli(DTL), flashover in bus isolator at 220kV side of 220/66kV 100 MVA transformer-2 at Mehrauli(DTL) occurred. 100 MVA transformer-2 at Mehrauli(DTL) tripped on E/F protection. At the same time, 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 tripped on R-Y phase to phase fault in Z-2. (exact nature and location of fault yet to be received). iv)As per PMU at Bamnoli(DV), R-Y phase to phase fault with delayed clearance of ~400 msec is observed. v)As 220KV Tughlakabad(PG)-Mehrauli(DV) (DTL) Ckt-1 was the only source for load of Mehrauli(DTL), complete station got blackout after tripping of the line. vi)As per SCADA, change in demand of approx 375 MW in Delhi control area is observed however as reported by SLDC-Delhi, approx 240 MW load affected during the event. vii)As reported, load was | grid_india_gd/grid_events/2026-05-01
G00296 | 2026-05 | 41 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-28T17:35 | 2026-05-28T18:20 | 0.75 | 322 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 322 MW at Vishnuprayag HEP was observed. | 41 GD-1 Uttar Pradesh 28-05-2026 17:35 28-05-2026 18:20 00:45 322 0 51.74% 0.00% 62229 78562 i)Power of 110*4MW Vishnuprayag HEP evacuates through 400 KV Alaknanda GVK (UPC)-Muzaffarnagar(UP) Ckt and 400 KV Alaknanda GVK(UPC)-Vishnuprayag(JP) (UP) Ckt. ii)During antecedent condition, 110 MW Vishnuprayag HPS - UNIT 1, 2 & 3 were on running condition and were generating approx 110 MW , 111 MW and 101 MW respectively (as per SCADA). 400 KV Alaknanda GVK(UPC)-Vishnuprayag(JP) (UP) Ckt was already under tripped condition (As reported, 400 KV Alaknanda GVK(UPC)-Vishnuprayag(JP) (UP) Ckt tripped at 16:51 hrs on R-N phase to earth fault with fault distance of 52.81 km from Vishnuprayag end. As per DR, fault sensed in zone-1 at Alaknanda end and fault current was ~2.37kA from Alaknanda end). iii)As reported, at 17:35 hrs, 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt tripped on Y-B phase to phase fault with fault distance of 44.76 km from Vishnuprayag end. As per DR, fault sensed in zone-1 at Muzaffarnagar end and fault current was Iy=~2.308kA, Ib= ~2.727kA from Muzaffarnagar end. iv)With the tripping of 400 KV Muzaffarnagar(UP)-Vishnuprayag(JP) (UP) Ckt, generating units of Vishnuprayag HEP tripped on over-frequency protection operation due to loss of evacuation path. v)Due to this event, complete blackout occurred at 400kV Vishnuprayag HPS(UP) S/s. i)As per PMU at Muzaffarnagar(UP), Y-B phase to phase fault was observed with fault clearance time of 80 ms. vi)As per SCADA, gener | grid_india_gd/grid_events/2026-05-01
G00297 | 2026-05 | 39 | GI-2 | Uttar Pradesh | UP | Northern | 2026-05-28T23:09 | 2026-05-29T01:25 | 2.27 | 0 | 100 | FALSE | FALSE | FALSE | FALSE | FALSE | 39 GI-2 Uttar Pradesh 28-05-2026 23:09 29-05-2026 01:25 02:16 0 100 0.00% 13.72% 56513 72897 i)400/220/132KV Parichha(UP) has double main and transfer bus scheme in both 400kV and 220kV level. 210 MW Unit-3 & 4 are connected at 220kV level and 250 MW Unit-5 & 6 are connected at 400kV level. ii)Durin | 39 GI-2 Uttar Pradesh 28-05-2026 23:09 29-05-2026 01:25 02:16 0 100 0.00% 13.72% 56513 72897 i)400/220/132KV Parichha(UP) has double main and transfer bus scheme in both 400kV and 220kV level. 210 MW Unit-3 & 4 are connected at 220kV level and 250 MW Unit-5 & 6 are connected at 400kV level. ii)During antecedent condition, 220kV Parichha-Jhansi(UP) Ckt-1 & 2 and 220kV Parichha-Mauranipur(UP) were already under shutdown. 220kV Parichha-Moth was not carrying any active power as 220kV Moth-Orai Ckt already tripped at 23:00 hrs. iii)As reported, at 23:09 hrs, 220kV Parichha-Orai (UP) Ckt-3 tripped on B-N phase to earth fault; fault sensed in zone-1 at Parichha end (exact location of fault yet to be shared). iv)During the same time, 400 KV Orai-Parichha (UP) Ckt-1 & 2 also tripped due to tower collapse (exact nature and location of fault yet to be shared). v)As per PMU at Mainpuri(PG), B-N phase to earth fault overlapped partially with R-Y phase to phase fault followed by R-N phase to earth fault immediately followed by Y-N phase to earth fault was observed with fault clearance time of 80 ms each. vi)As per SCADA, change in demand of approx 100 MW was observed at UP control area. 1) 400 KV Orai-Parichha (UP) Ckt-1 2) 400 KV Orai-Parichha (UP) Ckt-2 3) 220kV Parichha-Orai (UP) Ckt-3 | grid_india_gd/grid_events/2026-05-01
G00298 | 2026-05 | 37 | GI-2 | Haryana | HR | Northern | 2026-05-28T23:11 | 2026-05-29T01:54 | 2.72 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 37 GI-2 Haryana 28-05-2026 23:11 29-05-2026 01:54 02:43 0 0 0.00% 0.00% 56406 72815 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole) (as per SCADA). ii)As reported, at 23:11 hrs, 800 KV HVDC Kurukshetra(P | 37 GI-2 Haryana 28-05-2026 23:11 29-05-2026 01:54 02:43 0 0 0.00% 0.00% 56406 72815 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole) (as per SCADA). ii)As reported, at 23:11 hrs, 800 KV HVDC Kurukshetra(PG) Pole-2 & 4 tripped on DC line fault with fault distance of 538.766km from Kurukshetra end (Tower loc. no. 2010). iii)As per PMU at Kurukshetra (PG), 3-ph fault was observed with fault clearing time of 80 ms. iv)As per SCADA, no change in demand was observed in Haryana control area. Change in power order of approx 1150 MW was observed. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 | grid_india_gd/grid_events/2026-05-01
G00299 | 2026-05 | 40 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-28T23:58 | 2026-05-29T01:37 | 1.65 | 492 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | v)As per SCADA, generation loss of approx 492 MW occurred at Parichha(UP) at 23:58 hrs (224 MW at 220kV Parichha and 268 MW at 400kV Parichha). | 40 GD-1 Uttar Pradesh 28-05-2026 23:58 29-05-2026 01:37 01:39 492 0 91.77% 0.00% 53615 71778 i)As reported, at 23:33 hrs, 220/132kV 100 MVA ICT-1 and 160 MVA ICT-2 at Parichha(UP) tripped on REF protection operation. ii)Finally, at 23:58 hrs, 220kV Parichha-Orai (UP) Ckt-1, 220kV Parichha-Bharthana (UP) Ckt and 220kV Parichha-Mahoba (UP) Ckt tripped on overload. iii)With tripping of all 220kV and 400kV lines at Parichha(UP), 210 MW Unit-3 & 4 and 250 MW Unit-5 & 6 at Parichha (UP) tripped on over-frequency protection operation due to loss of evacuation path and complete blackout occurred at 400/220/132KV Parichha(UP). iv)As per PMU at Mainpuri(PG), no fault was observed in the system. v)As per SCADA, generation loss of approx 492 MW occurred at Parichha(UP) at 23:58 hrs (224 MW at 220kV Parichha and 268 MW at 400kV Parichha). 1) 220kV Parichha-Orai (UP) Ckt-1 2) 220kV Parichha-Bharthana (UP) Ckt 3) 220kV Parichha-Mahoba (UP) Ckt 4) 210 MW Unit-3 at Parichha (UP) 5) 210 MW Unit-4 at Parichha (UP) 6) 250 MW Unit-5 at Parichha (UP) 7) 250 MW Unit-6 at Parichha (UP) | grid_india_gd/grid_events/2026-05-01
G00300 | 2026-05 | 42 | GD-1 | Uttar Pradesh | UP | Northern | 2026-05-29T00:12 | 2026-05-29T12:30 | 12.3 | 0 | 50 | FALSE | FALSE | FALSE | FALSE | FALSE | 42 GD-1 Uttar Pradesh 29-05-2026 00:12 29-05-2026 12:30 12:18 0 50 0.00% 7.01% 53469 71276 i)During antecedent condition, 220kV Mahoba-Parichha(UP) Ckt was already under tripped condition (line tripped on B-N phase to earth fault at 23:58 hrs on 28.05.2026). ii)As reported, at 00:12 hrs, 220 KV Maho | 42 GD-1 Uttar Pradesh 29-05-2026 00:12 29-05-2026 12:30 12:18 0 50 0.00% 7.01% 53469 71276 i)During antecedent condition, 220kV Mahoba-Parichha(UP) Ckt was already under tripped condition (line tripped on B-N phase to earth fault at 23:58 hrs on 28.05.2026). ii)As reported, at 00:12 hrs, 220 KV Mahoba-Banda(UP) Ckt tripped on B-N Phase to earth fault with fault current of 3.47kA and fault distance of 35.932km from Banda(UP) end; fault sensed in zone-1 at Banda(UP) end. iii)Due to tripping of both the 220kV lines, supply failed from HV side of 220/132kV 100MVA ICT-1 and 160MVA ICT-2 at Mahoba(UP) and complete blackout occurred at 220/132kV Mahoba(UP) S/s. iv)As per PMU at Mainpuri(UP), Y-B Phase to phase fault followed by R-Y phase to phase fault followed by 3-ph fault was observed with fault clearance time of 80 ms each. v)As per SCADA, change in demand of approx 45 MW in UƩar Pradesh control area was observed. As reported by SLDC UP , load loss of approx 50 MW occurred. Load normalized through charging of 220kV Mahoba-Parichha(UP) Ckt at 02:16 hrs. 1) 220 KV Mahoba-Banda(UP) Ckt | grid_india_gd/grid_events/2026-05-01
G00301 | 2026-05 | 69 | GD-1 | Gujarat | GJ | Western | 2026-05-29T12:51 | 2026-05-29T19:15 | 6.4 | 420 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 420 MW occurred at GSEC(S) plant due to the loss of evacuation path. | 23 GD-1 Gujarat 29-05-2026 12:51 29-05-2026 19:15 06:24 420 - 0.53% - 79967 70396 Complete outage of 400KV GSEC(S): At 12:51 hrs on 29-05-2026, 400KV GSEC(S)-KPS2 tripped due to B-phase to Earth fault due to over voltage protection. Generation loss of 420 MW occurred at GSEC(S) plant due to the loss of evacuation path. 1.400KV GSEC(S)-KPS2-1 | grid_india_gd/grid_events/2026-05-01
G00302 | 2026-05 | 70 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-29T23:13 | 2026-05-30T01:37 | 2.4 | 163 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 163 MW occurred due to the tripping of JP Bina Unit 2 (250 MW). | 24 GD-1 Madhya Pradesh 29-05-2026 23:13 30-05-2026 01:37 02:24 163 - 0.19% - 84965 72880 Complete outage of 400 kV J P Bina: At 23:13 hrs on 29-05-2026, 400 kV JP Bina – Bina (PG), 400 kV JP Bina- Bina (MP) & JP Bina Unit 2 (250 MW) tripped on Bus bar protection operation at 400 kV JP Bina due to 400 kV side R phase Horizontal Centre Break isolator (89-T) of Generating Transformer 2 opened during heavy wind and thunder storm & resulted in sparking. Generation loss of 163 MW occurred due to the tripping of JP Bina Unit 2 (250 MW). 1. 400 kV JP Bina – Bina (PG) 2. 400 kV JP Bina- Bina (MP) 3. JP Bina Unit 2 (250 MW) | grid_india_gd/grid_events/2026-05-01
G00303 | 2026-05 | 43 | GD-1 | Rajasthan | RJ | Northern | 2026-05-30T14:36 | 2026-05-30T17:11 | 2.58 | 253 | 0 | TRUE | TRUE | FALSE | FALSE | TRUE | Generation loss of approx 253 MW occurred (67 MW at ARP1PL and 196 MW at ARP3PL). | 43 GD-1 Rajasthan 30-05-2026 14:36 30-05-2026 17:11 02:35 253 0 41.41% 0.00% 61092 58868 i)400kV Ayana Solar(IP) is connected at Bikaner(PG) at 400kV level and total generation of ARP1PL and ARP3PL evacuates through 400 KV Bikaner(PG)-AYANA1 SL_BKN_PG (ARP1PL) (ARP1PL) Ckt. ii)During antecedent condition, ARP1PL and ARP3PL were generating approx 67 MW and 196 MW respectively and 400 KV Bikaner(PG)-AYANA1 SL_BKN_PG (ARP1PL) (ARP1PL) Ckt was carrying total 253 MW (as per SCADA). iii)As reported at 14:36 hrs, 400 KV Bikaner(PG)-AYANA1 SL_BKN_PG (ARP1PL) (ARP1PL) Ckt tripped from Bikaner(PG) end on R-N phase to earth fault (exact reason, nature and location of fault yet to be shared) with fault current of 22.794kA from Bikaner(PG) end (as per DR) due to heavy wind & sandstorm in RE Pocket. iv)Due to tripping of this evacuating line, complete blackout occurred at 400kV Ayana Solar(IP) (both ARP1PL and ARP3PL). v)As per PMU at Bikaner(PG), R-N phase to earth fault was observed with fault clearance time of 80ms. vi)As per SCADA, dip in NR Total Solar Generation of approx 640 MW was observed among which 384 MW recovered within 1 minute. Generation loss of approx 253 MW occurred (67 MW at ARP1PL and 196 MW at ARP3PL). 1) 400 KV Bikaner(PG)-AYANA1 SL_BKN_PG (ARP1PL) (ARP1PL) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the M | grid_india_gd/grid_events/2026-05-01
G00304 | 2026-05 | 44 | GD-1 | Himachal Pradesh | HP | Northern | 2026-05-30T21:44 | 2026-05-31T01:53 | 4.15 | 141 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 111 MW at Sawrakuddu HEP and 30 MW at Naitwar Mori HEP occurred. | 44 GD-1 Himachal Pradesh 30-05-2026 21:44 31-05-2026 01:53 04:09 141 0 26.85% 0.00% 52507 60362 i)Generation of Naitwar Mori HEP and Sawrakuddu HEP evacuates through 400/220kV Gumma ICTs via 220kV Hatkoti-Gumma D/C. Sawrakuddu is directly connected to Hatkoti from one line and with LILO at Naitwar Mori in second line. 400/220kV 315 MVA ICT-1 & 2 at Gumma(HP) are charged in same dia. ii)During antecedent condition, all three 37 MW units at Sawrakuddu HEP was running and generating approx 111 MW total, at Naitwar Mori HEP only one 30 MW unit was running and generating ~30 MW. 400kV Bus-1 at Gumma(HP) was under shutdown and therefore 400/220kV 315 MVA ICT-2 was charged through Tie CB only. iii)As reported, at 21:44 hrs, 400/220kV 315 MVA ICT-1 at Gumma(HP) tripped due to operation of stage-2 of GIS gas low protection. As 400/220kV 315 MVA ICT-2 at Gumma(HP) was on same dia and charged through tie CB only, it also tripped simultaneously. iv)After tripping of both 400/220kV 315 MVA ICTs at Gumma(HP), all running units at Sawrakuddu HEP and Naitwar Mori HEP tripped due to loss of evacuation path. v)As per PMU at N. Jhakri HEP(SJVN), no fault in system is observed. vi)As per SCADA, generation loss of approx 111 MW at Sawrakuddu HEP and 30 MW at Naitwar Mori HEP occurred. No change in demand of HP control area is observed. 1) 400/220 KV 315 MVA ICT 1 AT Gumma(HP) 2) 400/220 KV 315 MVA ICT 2 AT Gumma(HP) 3) 37 MW Unit-1 at Sawrakuddu(HP) 4) 37 MW Unit-2 at Sawrakuddu(HP) 5) 37 MW Unit | grid_india_gd/grid_events/2026-05-01
G00305 | 2026-05 | 71 | GD-1 | Madhya Pradesh | MP | Western | 2026-05-30T22:29 | 2026-05-31T01:25 | 2.93 | 59 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 42 MW & 17 MW occurred at 220 kV Malwa (Blueleaf) & 220 kV Agar Malwa Wind Power Plants respectively hence 220 kV Malwa (Blueleaf) Wind Power Plant went dark. | 25 GD-1 Madhya Pradesh 30-05-2026 22:29 31-05-2026 01:25 02:56 59 - 0.07% - 81102 70547 Complete outage of 220 kV Malwa (Blueleaf): At 22:29 hrs on 30-05-2026, Malwa (Blueleaf)- Pachora line tripped on R-E fault. Generation loss of 42 MW & 17 MW occurred at 220 kV Malwa (Blueleaf) & 220 kV Agar Malwa Wind Power Plants respectively hence 220 kV Malwa (Blueleaf) Wind Power Plant went dark. At the same time, 400 kV Pachora- Bhopal 2 tripped on R-E fault at Pachora end only. 220/33 kV Agar Malwa ICT 1 also tripped at the same time on REF protection operation. 1. Malwa (Blueleaf)- Pachora-1 2. 220/33 kV Agar Malwa ICT-1 3. 400 kV Pachora- Bhopal 2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 TAMILNADU 02-05-2026 18:39 02-05-2026 20:31 01:52 143 0 0.31% 0.00% 45547.6 54029.04 Complete Outage of 230kV JSW_Vilanthikulam of JSW_RE 230 kV JSW_Vilanthikulam generating station(wind) radially connected 230 kV TTGS station through 230KV-TTGS-JSW_Vilathikulam_300MW-1 line. The triggering incident was R-G fault due to inclement weather. Although A/R operated at both ends but at TTGS end 3 phase tripping was observed without any fault and line is holding from JSW_Vilathikulam end. As the line is a radial feeder , the tripping of the line at TTGS station led to complete outage of 230kV JSW_Vilanthikulam station. 230KV-TTGS-JSW_Vilathikulam_300MW-1 2 GD - 1 | grid_india_gd/grid_events/2026-05-01
G00306 | 2026-05 | 46 | GI-2 | Haryana | HR | Northern | 2026-05-31T18:45 | 2026-05-31T20:21 | 1.6 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 46 GI-2 Haryana 31-05-2026 18:45 31-05-2026 20:21 01:36 0 0 0.00% 0.00% 47338 55714 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~2000 MW power from Champa to Kurukshetra (~500 MW on each Pole) (as per SCADA). ii)As reported, at 18:45 hrs, 800 KV HVDC Kurukshetra(PG) Pole-2 & 4 tripped on DC line fault with fault distance of 442.796 km from Kurukshetra end (Tower loc. no. 2264- 2265). iii)As per PMU at Kurukshetra (PG), no fault was observed in the system; however fluctuation in voltage was observed. iv)As per SCADA, no change in demand in Haryana control area and no change in power order was observed. The power order of Pole-1 & 3 ramped up to compensate the Power of Pole 2 & 4. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-05-01
G00307 | 2026-05 | 45 | GI-2 | Uttar Pradesh | UP | Northern | 2026-05-31T19:49 | 2026-05-31T22:11 | 2.37 | 595 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of ~595 MW is observed due to tripping of 660MW Unit-1 at Ghatampur(UP). | 45 GI-2 Uttar Pradesh 31-05-2026 19:49 31-05-2026 22:11 02:22 595 0 118.34% 0.00% 50277 62425 i)765/400/132KV Ghatampur(UP) has one and half breaker scheme in 765KV, 400KV and double main bus scheme in 132KV. It comprises of 3 X 660MW of generation. Unit-3 and 400kV system at Ghatampur is yet to be commissioned. ii)During antecedent condition, 660MW GHATAMPUR TPS - UNIT 1 was generating 595 MW . 765kV Ghatampur_TPS(UP)-Agra Fatehabad(UP) line was carrying ~591 MW and 765 KV RAMPUR_PRSTL-GHATAMPUR_TPS (UP) CKT-1 was under tripped condition since 17:14 hrs on same day due to permanent R-N fault. iii)As reported, at 19:49 hrs, 765kV Ghatampur_TPS(UP)-Agra Fatehabad(UP) line tripped on R-N fault. As per DR of Agra Fatehabad(UP) end, R-N fault in Z-1 with successful A/R at Ghatampur end and no A/R with SOTF trip is observed at Agra Fatehabad end. Fault distance and fault current was 1.8kA and 66.8km from Ghatamapur end and 5.09kA and 125.5km from Agra Fatehabad end. Reason of SOTF trip at Agra Fatehabad end yet to be received. iv)As 765kV Ghatampur_TPS(UP)-Agra Fatehabad(UP) line was the only evacuation path available, 660 MW Unit-1 at Ghatampur TPS tripped due to loss of evacuation path. v)As per PMU at Agra(PG), R-N phase to earth fault with clearance time of 80 msec is observed. vi)As per SCADA, generation loss of ~595 MW is observed due to tripping of 660MW Unit-1 at Ghatampur(UP). 1) 765 KV RAMPUR_PRSTL -GHATAMPUR_TPS (UP) CKT-1 2) 765 KV Agra Fatehabad-GHATAMPUR_TPS (UP) CKT | grid_india_gd/grid_events/2026-05-01
G00308 | 2026-06 | 26 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-01T14:20 | 2026-06-01T18:52 | 4.53 | 190 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 190 MW Occurred at Malwa (Blueleaf) due to loss of evacuation path. | 1 GD-1 Madhya Pradesh 01-06-2026 14:20 01-06-2026 18:52 04:32 190 - 0.21% - 90795 74790 Complete outage of 220 kV Malwa (Blueleaf Energy): At 14:20 hrs / 01-06-2026, 220 kV Pachora-Malwa-1 tripped on line differential protection operation R-E Fault. All three phases tripped at Malwa end for a fault a single line to ground fault (R-E fault), Auto recloser not operated, which is undesirable for a single line to ground fault. Autorecloser was successful at Pachora End (PMU Current Plot (220 kV Pachora-Malwa-1) and tripped after 332 msec as fault reappeared in reclaim time. Suspension insulator was found damaged/dislocated at Tower No. AP-10, as reported by line patrolling team, Blueleaf. Generation loss of 190 MW Occurred at Malwa (Blueleaf) due to loss of evacuation path. Tripping of following Elements: 1. 220 kV Pachora-Malwa-1 S/C | grid_india_gd/grid_events/2026-06-01
G00309 | 2026-06 | 28 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-01T14:44 | 2026-06-01T18:59 | 4.25 | 108 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 108 MW occurred at 220 kV Shajapur Unit-8 due loss of the evacuation path. | 3 GD-1 Madhya Pradesh 01-06-2026 14:44 01-06-2026 18:59 04:15 108 - 0.12% - 92232 76148 Complete outage of 220 kV Shajapur Unit8 (Talletuttayi):At 14:44 hrs/01.06.2026, the 220 kV Shajapur Unit-8 – Pachora line tripped due to a B-phase to Earth (B-E) fault. Generation loss of 108 MW occurred at 220 kV Shajapur Unit-8 due loss of the evacuation path. Tripping of following Elements: 1. 220 kV Shajapur Unit-8 – Pachora | grid_india_gd/grid_events/2026-06-01
G00310 | 2026-06 | 27 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-01T15:35 | 2026-06-02T01:50 | 10.25 | 75 |  | FALSE | TRUE | FALSE | FALSE | TRUE | As a consequence, a generation loss of 75 MW was reported at SBES Pritamnagar Tripping of following Elements: 1. | 2 GD-1 Madhya Pradesh 01-06-2026 15:35 02-06-2026 01:50 10:15 75 - 0.09% - 79424 69707 Complete outage of 220 kV Pritam Nagar (Adani): At 15:35 hrs/01-06-2026, the 220 kV Indore-Pritamnagar transmission line tripped due to a Y-phase to Earth fault due to jumper pilot insulator failure at tower no. 38A, resulting in the loss of the evacuation path and causing the 220 kV Pritamnagar Wind Power Plant to go dark. As a consequence, a generation loss of 75 MW was reported at SBES Pritamnagar Tripping of following Elements: 1. 220 kV Indore-Pritamnagar | grid_india_gd/grid_events/2026-06-01
G00311 | 2026-06 | 1 | GD-1 | Rajasthan | RJ | Northern | 2026-06-01T20:50 | 2026-06-01T23:57 | 3.12 | 268 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | v)As per SCADA, generation loss of approx 5 MW at AHEJ3L(IP) and change in wind generation of approx 263 MW in Rajasthan control area were observed. | 1 GD-1 Rajasthan 01-06-2026 20:50 01-06-2026 23:57 03:07 268 0 46.24% 0.0 0% 57962 69676 i)Generation of 220kV AHEJ3L(IP) station evacuates through 220 KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt which is further connected to 220/33 kV 150 MVA ICT 1 & 2 at AHEJ3L(IP). ii)During antecedent condition, 220kV AHEJ3L(IP) station was generating approx 5 MW (as per SCADA). iii)As reported, at 20:50hrs, 220 KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt tripped on R-N phase to earth fault (exact nature, location and reason of fault yet to be shared) which led to complete blackout out of 220kV AHEJ3L(IP) S/s. iv)As per PMU at Fatehgarh2(PG), R-N phase to earth fault was observed with fault clearing time of 80ms. Voltage dipped upto 0.854 pu during fault. v)As per SCADA, generation loss of approx 5 MW at AHEJ3L(IP) and change in wind generation of approx 263 MW in Rajasthan control area were observed. 1) 220 KV Fatehgarh_II(PG)-AHEJ3L PSS HB_FGRAH_PG (AHEJ3L) (AHEJ3L) Ckt | grid_india_gd/grid_events/2026-06-01
G00312 | 2026-06 | 2 | GD-1 | Rajasthan | RJ | Northern | 2026-06-01T21:23 | 2026-06-01T23:39 | 2.27 | 313 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | vii)As per PMU at AWPS1(IP), generation loss of approx 154 MW occurred at AHEJ4L PSS3 (AWPS1) (IP). | 2 GD-1 Rajasthan 01-06-2026 21:23 01-06-2026 23:39 02:16 313 0 54.59% 0.0 0% 57332 70697 i)Generation of 220 kV AHEJ4L PSS3 (AWPS1) (IP) and 220 kV ASEJOL_wind(IP) station evacuate through 220 KV Adani RenewPark_SL_ FGARH_FBTL (AREPRL)-AHEJ4L PSS 3 HB_FGRAH_FBTL (AWPS1) (AREPRL) Ckt and 220 KV ASEJOL_HB FTGH2 -ASEJOL_WIND FTGH2 (ASEJOL) Ckt respectively. ii)During antecedent condition, 220 kV AHEJ4L PSS3 (AWPS1) (IP) and 220 kV ASEJOL_wind(IP) were generating approx 154 MW (as per PMU) and 36 MW (as per SCADA) respectively. iii)As reported, at 21:23 hrs, 220 KV Adani RenewPark_SL_ FGARH_FBTL (AREPRL)-AHEJ4L PSS 3 HB_FGRAH_FBTL (AWPS1) (AREPRL) Ckt tripped on Y-N phase to earth fault with fault current of Iy=~2.74 kA and fault distance of 42.76 km from AWPS1 end; fault duration was 473.4 ms; fault sensed in zone-2 at AHEJ4L PSS3 (AWPS1) end (as per EL). This led to complete blackout out of 220 kV AHEJ4L PSS3 (AWPS1) (IP) S/s. iv)During the same time, 220 KV ASEJOL_HB FTGH2 -ASEJOL_WIND FTGH2 (ASEJOL) Ckt also successfully auto-reclosed from ASEJOL_wind end on R-N phase to earth fault with fault current of Ir=~6.535 kA from ASEJOL_wind end; fault sensed in zone-1 at ASEJOL_wind end (as per DR). However line finally tripped on consecutive R-N phase to earth fault within reclaim time. v)As per PMU at Fatehgarh2(PG), 21:22:28:320 hrs and 21:22:32:280 hrs respectively, two consecutive R-N phase to earth faults within reclaim time were observed with fault clearing time of 80ms each. | grid_india_gd/grid_events/2026-06-01
G00313 | 2026-06 | 3 | GD-1 | Rajasthan | RJ | Northern | 2026-06-01T21:31 | 2026-06-04T00:03 | 50.53 | 111 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | v)Due to tripping of both 400 KV Fatehgarh_III(PG)-Fatehgarh_IV(F4TL) (F4TL) Ckt-1 & 2, complete blackout occurred at 400/220kV Fatehgarh4(IP) and complete loss of evacuation occurred at 220kV Amp Energy(IP) resulting in 70 MW wind generation loss at 220kV Amp Energy(IP). | 3 GD-1 Rajasthan 01-06-2026 21:31 04-06-2026 00:03 50:32 111 0 19.32% 0.0 0% 57446 71024 i)Generation of 220kV Amp Energy(IP) station evacuates through 220kV Fatehgarh_IV(F4TL)-Amp Energy(IP) Ckt via 400/220kV 500 MVA ICT-1, 2, 3, 4, & 5 at Fatehgarh_IV(F4TL) which is further connected to 400 KV Fatehgarh_III(PG)-Fatehgarh_IV(F4TL) (F4TL) Ckt-1 & 2. ii)During antecedent condition, 220kV Amp Energy(IP) station was generating approx 70 MW (as per SCADA). iii)As reported, at 21:31 hrs, 400 KV Fatehgarh_III(PG)-Fatehgarh_IV(F4TL) (F4TL) Ckt-2 tripped due to R & B-phase broken LA and 400 KV Fatehgarh_III(PG)- Fatehgarh_IV(F4TL) (F4TL) Ckt-1 tripped due to R-phase broken LA. iv)As per PMU, at 21:31:21:800 hrs, 400 KV Fatehgarh_III(PG)-Fatehgarh_IV (F4TL) (F4TL) Ckt-2 tripped on R-Y phase to phase fault and at 21:31:22:920 hrs, 400 KV Fatehgarh_III(PG)-Fatehgarh_IV(F4TL) (F4TL) Ckt-1 tripped on R-Y phase to phase fault (exact nature and location of fault yet to be shared). v)Due to tripping of both 400 KV Fatehgarh_III(PG)-Fatehgarh_IV(F4TL) (F4TL) Ckt-1 & 2, complete blackout occurred at 400/220kV Fatehgarh4(IP) and complete loss of evacuation occurred at 220kV Amp Energy(IP) resulting in 70 MW wind generation loss at 220kV Amp Energy(IP). vi)As per PMU at Fatehgarh3(PG), two consecutive R-Y phase to phase fault was observed with fault clearing time of 80ms each. vii)As per SCADA, change in NR wind generation of approx 111 MW and Rajasthan wind generation of approx 88 MW were obser | grid_india_gd/grid_events/2026-06-01
G00314 | 2026-06 | 29 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-01T21:35 | 2026-06-01T22:09 | 0.57 | 340 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Consequently both the Unit-1 & 2 had tripped, resulted in a generation loss of 340 MW at 400 kV JP Bina S/S. | 4 GD-1 Madhya Pradesh 01-06-2026 21:35 01-06-2026 22:09 00:34 340 - 0.40% - 84951 65623 Complete outage of 400 kV JP Bina: At 21:35:14.038 hrs/ 01-06-2026, 400kV JP Bina-Bina(PG) transmission line, 400kV JP Bina-Bina(MP) transmission line, and JP Bina Unit -1 & 2 (250MW each) tripped. Due to failure of the locking arrangement of the GT-2 R-phase HCB Isolator (4-589T) inadvertently opened, resulting in R-Y fault which led to tripping of 400 kV Bus-2 on Bus bar protection. Simultaneously 400 kV Bus -1 also tripped due to non-updation of isolator status which was a mal-operation. Consequently both the Unit-1 & 2 had tripped, resulted in a generation loss of 340 MW at 400 kV JP Bina S/S. Tripping of following Elements: 1. 400kV JP Bina-Bina(PG) 2. 400kV JP Bina-Bina(MP) 3. 400 kV JP Bina-Bus-1&2 4. JP Bina Unit-1&2 | grid_india_gd/grid_events/2026-06-01
G00315 | 2026-06 | 4 | GI-2 | Rajasthan | RJ | Northern | 2026-06-01T22:45 | 2026-06-02T02:22 | 3.62 | 703 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, Generation loss of approx 703 MW was observed at Rajwest(RW). | 4 GI-2 Rajasthan 01-06-2026 22:45 02-06-2026 02:22 03:37 703 0 120.02% 0. 00% 58576 72498 i)400/220kV Rajwest(RW) has one and half breaker scheme at 400kV level and double main bus and transfer bus scheme at 220kV level.ii)During antecedent condition, 135 MW Rajwest (IPP) LTPS - UNIT 1, 2, 3, 4, 5, 6, & 7 were in running condition and were generating approx 115 MW, 91 MW, 92 MW, 90 MW, 103 MW, 106 MW and 106 MW respectively (as per SCADA). 400 KV Barmer(RS)-Rajwest(RW) (RS) Ckt and 400 KV Rajwest(RW)-GSS Pachpadra (RS) Ckt were already under tripped condition since 20:48 hrs and 22:09 hrs respectively.iii)As reported, at 22:45 hrs, 400 KV Rajwest(RW)-Jodhpur (RS) Ckt tripped on B-N phase to earth fault due to tower collapse with fault current of 2.588 kA and fault distance of 64.2 km (30.8%) from Rajwest(RW) end; zone-1 distance protection operated at Rajwest end (as per DR). iv)During the same time, 400/220 KV 315 MVA ICT Rajwest(RS) also tripped due to overloading. As per DR, over-current protection operated in ICT.v)This resulted in the loss of the remaining 400 kV evacuation path from Rajwest and 135 MW Rajwest (IPP) LTPS - UNIT 3, 4, 5, 6, & 7 tripped on over-frequency due to loss of evacuation path. vi)It is observed that 135 MW Rajwest (IPP) LTPS - UNIT 1 & 2 which are connected to the 220 kV system and had an available evacuation path, also tripped during the same time (exact reason of tripping and nature of protection operated yet to be shared).vii)As per PMU at Jodh | grid_india_gd/grid_events/2026-06-01
G00316 | 2026-06 | 30 | GD-1 | Gujarat | GJ | Western | 2026-06-02T10:06 | 2026-06-02T14:28 | 4.37 | 95 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GD-1 Gujarat 02-06-2026 10:06 02-06-2026 14:28 04:22 95 - 0.12% - 78249 6 3073 Complete outage of 220 kV Kotdamadh: At 10:06 hrs/02-06-2026, the 220 kV Bhuj – Netra Kotda Madh transmission line tripped on B-phase to Earth fault due to throwing of a conducting object by an unknown person, resulting in a generation loss of 95 MW at Kotda madh S/S due to loss of evacuation path. | 5 GD-1 Gujarat 02-06-2026 10:06 02-06-2026 14:28 04:22 95 - 0.12% - 78249 6 3073 Complete outage of 220 kV Kotdamadh: At 10:06 hrs/02-06-2026, the 220 kV Bhuj – Netra Kotda Madh transmission line tripped on B-phase to Earth fault due to throwing of a conducting object by an unknown person, resulting in a generation loss of 95 MW at Kotda madh S/S due to loss of evacuation path. Tripping of following Elements: 1. 220 kV Bhuj – Netra Kotda Madh | grid_india_gd/grid_events/2026-06-01
G00317 | 2026-06 | 5 | GD-1 | Rajasthan | RJ | Northern | 2026-06-03T12:42 | 2026-06-03T12:52 | 0.17 | 566 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | viii)As per SCADA, change in NR total solar generation of approx 566 MW and generation loss of approx 410 MW at Saurya Urja were observed. | 5 GD-1 Rajasthan 03-06-2026 12:42 03-06-2026 12:52 00:10 566 0 87.02% 0.0 0% 65044 72915 i)Generation of 220kV Saurya Urja evacuates through 220 KV Bhadla(RS)-Saurya Urja Ckt-1 & 2. ii)During antecedent condition, 220kV Saurya Urja was generating approx 42 MW and 220 KV Bhadla(RS)-Saurya Urja Ckt-1 & 2 were carrying approx 197 MW and 213 MW respectively (as reported by SLDC Rajasthan). iii)As reported, at 12:42 hrs, 220 KV Bhadla(RS)-Saurya Urja Ckt-1 & 2 tripped during SPS mock testing of SPS at 400kV GSS Jodhpur(RS) and 400kV GSS Bhadla(RS) in case of tripping of 400kV Jodhpur-Kankroli Ckt. iv)As per SPS logic, with tripping of 400kV Jodhpur-Kankroli Ckt, SPS signal will be generated and following solar feeders shall be tripped instantaneously: 220kV Bhadla(RS)- M/s RSDCL D/C (Park capacity 340 MW), 220kV Bhadla(RS)-M/s Adani D/C (Park capacity 250 MW) and 220kV Bhadla(RS)-M/s Saurya Urja D/C (Park capacity 500 MW). v)It is evident from the above event that tripping was not disabled in 220 KV Bhadla(RS)-Saurya Urja Ckt-1 & 2 during SPS mock testing. vi)Due to tripping of both 220 KV Bhadla(RS)-Saurya Urja Ckt-1 & 2, complete blackout occurred at 220kV Saurya Urja due to loss of power evacuating path. vii)As per PMU at Bhadla(PG), no fault was observed in the system. viii)As per SCADA, change in NR total solar generation of approx 566 MW and generation loss of approx 410 MW at Saurya Urja were observed. 1) 220 KV Bhadla(RS)-Saurya Urja Ckt-1 2) 220 KV Bhadla(RS)-Saurya Urja | grid_india_gd/grid_events/2026-06-01
G00318 | 2026-06 | 42 | GI-2 | TAMILNADU |  |  | 2026-06-03T18:00 | 2026-06-03T18:06 | 0.1 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GI-2 TAMILNADU 03-06-2026 18:00 03-06-2026 18:06 00:06 0 0 0.00% 0.00% 4 8117.54 52816.02 Tripping of 400kV Bus-2 of 400kV Alamathy SS of TANTRANSCO As per the reports submitted, the triggering incident was R-G fault in 400kV Alamathy-Manali line due to failure of R phase supporting insulator whi | 15 GI-2 TAMILNADU 03-06-2026 18:00 03-06-2026 18:06 00:06 0 0 0.00% 0.00% 4 8117.54 52816.02 Tripping of 400kV Bus-2 of 400kV Alamathy SS of TANTRANSCO As per the reports submitted, the triggering incident was R-G fault in 400kV Alamathy-Manali line due to failure of R phase supporting insulator which eventually caused R-G fault in 400kV Bus-2. Immediately, 400kV Bus-2 BBP operated and all main breakers connected to 400kV Bus-2 tripped. This led to loss of power supply to 400kV Alamathy Bus-2. 400KV/230KV ALAMATHY-ICT-4, 400KV/110KV ALAMATHY- ICT-1, 400KV-VALLUR-ALAMATHY-2, 400KV-ALAMATHY- MANALI-1, 400KV-ALAMATHY-NCTPS_STAGE_II-1, 400KV- VALLUR-ALAMATHY-2 | grid_india_gd/grid_events/2026-06-01
G00319 | 2026-06 | 47 | GD-1 | West Bengal | WB | Eastern | 2026-06-04T11:52 | 2026-06-04T12:24 | 0.53 | 225 | 92 | FALSE | FALSE | FALSE | FALSE | FALSE | Total generation loss of 225 MW and load loss of 92 MW reported at 22kV Santaldih S/s. | 1 GD-1 WEST BENGAL 04-06-2026 11:52 04-06-2026 12:24 00:32 225 92 0.86% 0 .28% 26249 32402 Prior to the disturbance 220kV Santaldih bus was in split condition to control the loading of 220kV Chandil-Santaldih line. During shifting of ST from 220kV main bus-1 to main bus-2, heavy flashover was observed in main bus -2 isolator which created bus fault in both buses. Due to flashover bus bar protection of 220kV main bus -1 & 2 operated and all elements connected through main bus 1 & 2 got tripped. 220kV Santaldih S/s became dead. Total generation loss of 225 MW and load loss of 92 MW reported at 22kV Santaldih S/s. 220 kV Main Bus-1 at Santaldih 220 kV Main Bus-2 at Santaldih 250 MWU#6 at Santaldih 220 KV Chandil- Santaldih 220 KV Santaldih – Asansol - 1 220 KV Santaldih – Asansol - 2 220 KV Santaldih – Raghunathpur - 1 220 KV Santaldih – Raghunathpur - 2 220 KV Santaldih – Hura-1 220 KV Santaldih – Hura-2 2*220/132 kV 130 MVA ICT at Santaldih 2 GI-II JHARKHAND 12-06-2026 16:47 12-06-2026 23:11 06:24 1237 0 4.17% 0. 00% 29660 27071 Prior to the event North Karanpura Unit-1 got tripped at 16:27 Hrs on 12/06/2026 on turbine bearing high vibration. Subsequently, at 16:47 Hrs on 12.06.2026, 400 kV Chandwa (PG) – North Karanpura (JUSNL) Ckt-II tripped on an R-E fault from North Karanpura end only with successful A/r from Chandwa end. Simultaneously, North Karanpura Units-2 and 3 tripped on turbine bearing high vibration. Total generation loss of 1237 MW reported at North Karanpura. NO | grid_india_gd/grid_events/2026-06-01
G00320 | 2026-06 | 8 | GD-1 | Uttarakhand | UK | Northern | 2026-06-04T14:56 | 2026-06-04T16:01 | 1.08 | 28 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, generation loss of approx 28 MW Singoli Bhatwari HEP were observed. | 8 GD-1 Uttarakhand 04-06-2026 14:56 04-06-2026 16:01 01:05 28 0 4.15% 0.0 0% 67440 73743 i)Power of 33*3 MW Singoli Bhatwari HEP evacuates through 220 KV Singoli Bhatwari (Singoli(LTUHP)) (end)-Srinagar(UK) (PTCUL) Ckt-1 & 2. ii)During antecedent condition, only 33MW unit-3 at Singoli Bhatwari HEP was running and generating approx 28 MW (Unit 1 and 2 were out of service as per schedule). iii)As reported, at 14:56 hrs, 220 KV Singoli Bhatwari(Singoli(LTUHP))-Srinagar(UK) (PTCUL) Ckt-1 tripped on B-N phase to earth fault with fault current of Ib=~1.657 kA and fault distance of 32.27 km from Srinagar end (as per EL). As per DR, fault clearing time was ~55 ms; zone-1 operated at Srinagar end; no A/R operation was observed. iv)Further, at the same time, 220 KV Singoli Bhatwari(Singoli(LTUHP))-Srinagar(UK) (PTCUL) Ckt-2 also tripped on R-B-N double phase to earth fault with fault current of Ir=~1.95 kA & Ib=~1.499 kA and fault distance of 52.18 km from Srinagar end (as per EL). As per DR, fault clearing time was ~65 ms; fault sensed in zone-1 at Srinagar end. v)Due to tripping of both 220 KV Singoli Bhatwari(Singoli(LTUHP))-Srinagar(UK) (PTCUL) Ckt-1 & 2, 33 MW Singoli Bhatwari(Singoli (LTUHP)) HPS - UNIT 3 tripped due to unavailability of power evacuating path and complete blackout occurred at 220kV Singoli Bhatwari HEP(Singoli(LTUHP)) S/s. vi)During the same time, 400/220kV 315 MVA ICT-1 at Srinagar(UK) also tripped due to differential protection operation. During investigation, | grid_india_gd/grid_events/2026-06-01
G00321 | 2026-06 | 31 | GD-1 | Maharashtra | MH | Western | 2026-06-04T15:06 | 2026-06-04T20:33 | 5.45 | 5 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Due to the loss of evacuation path, 220 kV Tandulwadi Wind Power Plant went dark, resulting in a generation loss of approximately 4.5 MW. | 6 GD-1 Maharashtra 04-06-2026 15:06 04-06-2026 20:33 05:27 5 - 0.01% - 793 50 69622 Complete outage of 220 kV Tandulwadi (Serentica): At 15:06 Hrs/ 04-06-2026, 220 kV Tandulwadi- Kallam line tripped at Tandulwadi end only on 86 & 96 Relay operation (Bus bar protection maloperation) alongwith 220 kV transformer and 220 kV Bus during R-Y fault on 33 kV feeder-2 (Bay-302) due to low sag issue between the two conductors. Due to the loss of evacuation path, 220 kV Tandulwadi Wind Power Plant went dark, resulting in a generation loss of approximately 4.5 MW. Tripping of following Elements: 1. 220 kV Tandulwadi- Kallam | grid_india_gd/grid_events/2026-06-01
G00322 | 2026-06 | 6 | GI-2 | Jammu and Kashmir | JK | Northern | 2026-06-04T16:42 | 2026-06-04T17:20 | 0.63 | 370 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | v)As per SCADA, generation loss of approx 370 MW was observed at Dulhasti(NH). | 6 GI-2 Jammu and Kashmir 04-06-2026 16:42 04-06-2026 17:20 00:38 370 0 62.61% 0.00% 59100 65733 i)During antecedent condition, 130 MW Dulhasti HPS - UNIT 1, 2 & 3 were in running condition and generating approx 123 MW, 129 MW and 118 MW respectively (as per SCADA). ii)As reported, at 16:42hrs, 400 KV Kishtwar(GIS)-Kishenpur(PG) (KwTL) Ckt-2 tripped on Y-N phase to earth fault with fault distance of 57.8 km from Kishenpur end and 59.1 km from Kishtwar end. As per DR, fault current was Iy=~4.738kA (~7.418kA during A/R) from Kishtwar end; zone-1 operated at Kishtwar end; A/R operated at Kishtwar end and A/R was unsuccessful due to permanent nature of fault. iii)During the same time, generator differential protection operated in all three units of Dulhasti(NH). As per DR, CT saturation was observed. As reported by NHPC, this maƩer was already taken up with relay OEM. iv)As per PMU at Kishenpur(PG), Y-N phase to earth fault with unsuccessful A/R was observed with fault clearing time of 80 ms. v)As per SCADA, generation loss of approx 370 MW was observed at Dulhasti(NH). 1) 400 KV Kishtwar(GIS)-Kishenpur(PG) (KwTL) Ckt-2 2) 130 MW Dulhasti HPS - UNIT 1 3) 130 MW Dulhasti HPS - UNIT 2 4) 130 MW Dulhasti HPS - UNIT 3 | grid_india_gd/grid_events/2026-06-01
G00323 | 2026-06 | 7 | GI-2 | Haryana | HR | Northern | 2026-06-04T17:03 | 2026-06-04T19:24 | 2.35 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GI-2 Haryana 04-06-2026 17:03 04-06-2026 19:24 02:21 0 0 0.00% 0.00% 571 09 64046 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole) (as per SCADA). ii)As reported, at 18:45 hrs, 800 KV HVDC Kurukshetra(PG) Pole-2 & 4 tripped on DC line fault with fault distance of 340.5 km from Kurukshetra end (Tower loc. no. 2541). iii)As per PMU at Kurukshetra (PG), no fault was observed in the system; however fluctuation in voltage was observed. iv)As per SCADA, no change in demand in Haryana control area was observed. Change in power order of approx 1325 MW occurred during the event. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 Details of Grid Events during the Month of June 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of June 2026 in Northern Region Elements Trippe | grid_india_gd/grid_events/2026-06-01
G00324 | 2026-06 | 32 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-04T23:41 | 2026-06-05T02:09 | 2.47 | 160 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 160 MW Occurred at Baradwada (TP Saurya) due to loss of evacuation path. | 7 GD-1 Madhya Pradesh 04-06-2026 23:41 05-06-2026 02:09 02:28 160 - 0.19% - 85658 69422 Complete outage of 220 kV Baradwara (TP Saurya):At 23:41 hrs / 04-06-2026, 220 kV Kawai-Baradwada-1 tripped on differential protection operation on B-E Fault. All three phases tripped for a fault in single phase (at both ends). No abnormality was found during patrolling. Generation loss of 160 MW Occurred at Baradwada (TP Saurya) due to loss of evacuation path. Tripping of following Elements: 1. 220 kV Kawai-Baradwada-1 | grid_india_gd/grid_events/2026-06-01
G00325 | 2026-06 | 33 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-06T17:01 | 2026-06-06T18:45 | 1.73 | 5 |  | TRUE | FALSE | FALSE | FALSE | TRUE | As a result of the line outage, the evacuation path for the generating station was lost, causing the 220 kV Shajapur Unit-6 (Burley) Solar Power Plant to become dark with a generation loss of 5 MW. | 8 GD-1 Madhya Pradesh 06-06-2026 17:01 06-06-2026 18:45 01:44 5 - 0.01% - 88700 74207 Complete outage of 220 kV Shajapur Unit6 (Burley): At 17:01 hrs/06-062026, the 220 kV Shajapur Unit-6 (Burley) – Shajapur Unit-7 (Dehripal) transmission line tripped on B-E (Phase-B to Earth) fault. As a result of the line outage, the evacuation path for the generating station was lost, causing the 220 kV Shajapur Unit-6 (Burley) Solar Power Plant to become dark with a generation loss of 5 MW. Tripping of following Elements: 1. 220 kV Shajapur Unit-6 (Burley) – Shajapur Unit-7 (Dehripal) Elements Tripped Details of Grid Events during the Month of June 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of June 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss o | grid_india_gd/grid_events/2026-06-01
G00326 | 2026-06 | 43 | GI-2 | TAMILNADU |  |  | 2026-06-06T18:58 | 2026-06-06T21:08 | 2.17 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GI-2 TAMILNADU 06-06-2026 18:58 06-06-2026 21:08 02:10 0 0 0.00% 0.00% 4 7847.05 53373.65 Tripping of 400kV Bus-1 of 400kV SEPC Generating station. As per the reports submitted, the triggering incident was B-G fault in 400kV SEPC Bus-1. Immedeately, 400kV Bus-1 BBP operated and all elements conne | 16 GI-2 TAMILNADU 06-06-2026 18:58 06-06-2026 21:08 02:10 0 0 0.00% 0.00% 4 7847.05 53373.65 Tripping of 400kV Bus-1 of 400kV SEPC Generating station. As per the reports submitted, the triggering incident was B-G fault in 400kV SEPC Bus-1. Immedeately, 400kV Bus-1 BBP operated and all elements connected to the bus tripped. SEPC - 400KV - Bus 1, 400KV-OTTAPIDARAM-SEPC-2 | grid_india_gd/grid_events/2026-06-01
G00327 | 2026-06 | 34 | GD-1 | Gujarat | GJ | Western | 2026-06-08T19:34 | 2026-06-08T19:56 | 0.37 | 31 |  | TRUE | FALSE | FALSE | FALSE | TRUE | 9 GD-1 Gujarat 08-06-2026 19:34 08-06-2026 19:56 00:22 31 - 0.03% - 89527 7 1087 Complete outage of 220 kV Rampar (Avaada Energy) : 19:34 Hrs/08-06-2026, 220 kV Rampar-Lakadia 1& 2 H/Ted from Rampar end and DT received at Lakadia end resultin in the 220 kV Rampar RE Solar Power Plant to become dark with a generation loss of 30.65 MW. | 9 GD-1 Gujarat 08-06-2026 19:34 08-06-2026 19:56 00:22 31 - 0.03% - 89527 7 1087 Complete outage of 220 kV Rampar (Avaada Energy) : 19:34 Hrs/08-06-2026, 220 kV Rampar-Lakadia 1& 2 H/Ted from Rampar end and DT received at Lakadia end resultin in the 220 kV Rampar RE Solar Power Plant to become dark with a generation loss of 30.65 MW. Prior to the event i.e. at 18:49 Hrs, while H/T of 400/220 kV Lakadiya ICT-2 at 765/400/220 kV Lakadiya Substation for planned S/D, 400/220 kV Lakadiya ICT-1 also tripped on 86A, B operation due to the ICT-1 LV-side (220 kV side) circuit breaker mal-operated and opened unintendedly. As per the protection scheme, the opening of the LV-side breaker initiated an inter-trip signal to the HV-side breaker, resulting in the complete tripping of ICT-1 and de-energization of 220 kV Bus-1 &2 at Lakadia, while the 400 kV and 765 kV networks remained healthy and in service. Tripping of following Elements: 1. 220 kV Rampar-Lakadia 1& 2 2. 400/220 kV Lakadiya ICT-1 3. 220 kV Lakadia Bus-1&2 | grid_india_gd/grid_events/2026-06-01
G00328 | 2026-06 | 9 | GI-1 | Delhi | DL | Northern | 2026-06-08T23:51 | 2026-06-09T00:30 | 0.65 | 0 | 146 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-1 Delhi 08-06-2026 23:51 09-06-2026 00:30 00:39 0 146 0.00% 17.40% 60 496 83920 i)220/33kV Masjid Moth(DTL) has double main bus scheme in both 220kV and 33kV voltage level. ii)During antecedent condition, 220/33 kV 100 MVA ICT 1 & 2 at Masjid Moth(DTL) were connected to 33kV Bus-1 and 220/33 kV | 9 GI-1 Delhi 08-06-2026 23:51 09-06-2026 00:30 00:39 0 146 0.00% 17.40% 60 496 83920 i)220/33kV Masjid Moth(DTL) has double main bus scheme in both 220kV and 33kV voltage level. ii)During antecedent condition, 220/33 kV 100 MVA ICT 1 & 2 at Masjid Moth(DTL) were connected to 33kV Bus-1 and 220/33 kV 100 MVA ICT 3 at Masjid Moth(DTL) was connected to 33kV Bus-2. 33kV Bus coupler was in OFF position. iii)As reported, at 23:51 hrs, 33kV Masjid Moth-Pushp Vihar (DTL) Ckt tripped on R-N phase to earth fault (exact reason, nature and location of fault yet to be shared). iv)During the same time, 220/33 kV 100 MVA ICT 2 at Masjid Moth(DTL) and 33kV incomers of 220/33 kV 100 MVA ICT 1 & 3 at Masjid Moth(DTL) tripped on differential protection operation. v)As per PMU at Mandaula(PG), R-N phase to earth fault was observed with delayed fault clearing time of 640 ms. vi)As per SCADA, change in demand of approx 177 MW was observed in Delhi control area. However, as reported by SLDC Delhi, total 146 MW load loss occurred. Details of load affected is attached in Annexure. 1) 220/33 kV 100 MVA ICT 1 at Masjid Moth(DTL) 2) 220/33 kV 100 MVA ICT 2 at Masjid Moth(DTL) 3) 220/33 kV 100 MVA ICT 3 at Masjid Moth(DTL) | grid_india_gd/grid_events/2026-06-01
G00329 | 2026-06 | 44 | GI-2 | Andhra Pradesh | AP | Southern | 2026-06-09T19:26 | 2026-06-09T21:22 | 1.93 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-2 ANDHRA PRADESH 09-06-2026 19:26 09-06-2026 21:22 01:56 0 0 0.00% 0.00% 52106.8 53984.1 7 Tripping of 400kV Kalpakka Bus-3 of APTRANSCO The triggering incident is the 4" IPS pipe connector failure in 400 kV Bay-424 (PGCIL-2 Bay) and came into contact with R-phase, resulting in R-G Bus fault i | 17 GI-2 ANDHRA PRADESH 09-06-2026 19:26 09-06-2026 21:22 01:56 0 0 0.00% 0.00% 52106.8 53984.1 7 Tripping of 400kV Kalpakka Bus-3 of APTRANSCO The triggering incident is the 4" IPS pipe connector failure in 400 kV Bay-424 (PGCIL-2 Bay) and came into contact with R-phase, resulting in R-G Bus fault in Bus-3. Subsequently, Bus-3 Busbar Protection operated and tripped all Bus-3 connected elements, namely 400kV Simhadri-Kalpakka-2, 400kV Kalpakka-Vemagiri AP-1, 400kV Gazuwaka-Kalpakka-2 and 400/220kV ICT-3 and Direct Transfer Trip signals were also transmitted to the corresponding remote substations. This led to the Tripping of 400kV Kalpakka Bus-3 of APTRANSCO 400KV-SIMHADRI-KALPAKKA-2, 400KV-KALPAKKA- VEMAGIRI_AP-1, 400KV-GAZUWAKA-KALPAKKA-2, 400KV/220KV KALPAKKA-ICT-3 | grid_india_gd/grid_events/2026-06-01
G00330 | 2026-06 | 35 | GD-1 | Gujarat | GJ | Western | 2026-06-10T04:58 | 2026-06-12T20:26 | 63.47 |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Gujarat 10-06-2026 04:58 12-06-2026 20:26 63:28 - - - - 82531 66181 Complete outage of 400 kV GIPCL PSS1 (GIPCL): At 04:58 hrs / 10-06-2026, 400 kV Khavda PS2-GIPCL PSS1-1 tripped on differential protection operation on Y-B phase to phase fault. Issue in Isolators at 400 kV Khavda PS2 (GIS S | 10 GD-1 Gujarat 10-06-2026 04:58 12-06-2026 20:26 63:28 - - - - 82531 66181 Complete outage of 400 kV GIPCL PSS1 (GIPCL): At 04:58 hrs / 10-06-2026, 400 kV Khavda PS2-GIPCL PSS1-1 tripped on differential protection operation on Y-B phase to phase fault. Issue in Isolators at 400 kV Khavda PS2 (GIS Substation) were identified and attended and line was charged at at 20:26 hrs / 12-06-2026. It is observed that readiness of line was given by GIPCL at 10:30 hrs / 10-06-2026 without consultation from remote end. No generation was present at GIPCL PSS1 (GIPCL) during the event. Tripping of following Elements: 1. 400 kV Khavda PS2-GIPCL PSS1-1 | grid_india_gd/grid_events/2026-06-01
G00331 | 2026-06 | 10 | GD-1 | Rajasthan | RJ | Northern | 2026-06-10T09:18 | 2026-06-10T11:06 | 1.8 | 222 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | v)As per PMU at SRI9PL(IP), generation loss of approx 105 MW occurred at Serentica9(IP). | 10 GD-1 Rajasthan 10-06-2026 09:18 10-06-2026 11:06 01:48 222 0 33.20% 0.0 0% 66873 73192 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) was generating approx 222 MW (as per SCADA). iii)As reported, at 09:18 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped on differential protection operation from SRI9PL end only due to heavy sandstorm (exact nature and location of fault yet to be shared). This led to complete blackout of 400kV Serentica 8 & 9 (IP) S/s. iv)As per PMU at Fatehgarh4(IP), 3-phase fault was observed with fault clearing time of 80ms. v)As per PMU at SRI9PL(IP), generation loss of approx 105 MW occurred at Serentica9(IP). vi)As per SCADA, generation loss of approx 222 MW at Serentica 8 & 9 (IP) and change in NR solar generation of approx 213 MW were observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt | grid_india_gd/grid_events/2026-06-01
G00332 | 2026-06 | 11 | GI-2 | Rajasthan | RJ | Northern | 2026-06-11T15:52 | 2026-06-11T16:20 | 0.47 | 0 | 518 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-2 Rajasthan 11-06-2026 15:52 11-06-2026 16:20 00:28 0 518 0.00% 62.7 6% 71201 82540 i)400/220kV Heerapura(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. 220/132kV Heerapura220(RS) also has double main and transfer bus scheme at 220kV | 11 GI-2 Rajasthan 11-06-2026 15:52 11-06-2026 16:20 00:28 0 518 0.00% 62.7 6% 71201 82540 i)400/220kV Heerapura(RS) has one and half breaker scheme at 400kV level and double main and transfer bus scheme at 220kV level. 220/132kV Heerapura220(RS) also has double main and transfer bus scheme at 220kV level. Both the substations are connected through bus sectionalisers at 220kV level.ii)As reported, at 15:52 hrs, during taking shutdown of 220kV Heerapura(RS)-KTPS Ckt, current unbalancing occurred due to opening of isolator at Heerapura(RS) which further created R-Y phase to phase fault (exact nature and location of fault yet to be shared).iii)Consequently, 400/220 KV 250 MVA ICT 1 & 3 at Heerapura(RS) tripped on over-current protection operation. As per DR of ICT-3, R-Y phase to phase fault was observed with fault current of Ir=~2.45kA, Iy=~2.29kA from Heerapura end and fault clearing time of ~840ms.iv)All 220kV lines connected from 400/220kV Heerapura(RS), i.e., 220 KV Heerapura(RS)-NPH Ckt, 220 KV Heerapura(RS)-Sanganer Ckt, 220 KV Heerapura(RS)-SEZ Ckt and 220 KV Heerapura(RS)-Phulera Ckt tripped on zone-4 protection operation at Heerapura(RS) end.v)As per SCADA SOE, 220 KV Heerapura220(RS)-Mansarovar Ckt, 220 KV Heerapura220(RS)-I.G.NagarCkt and 220 KV Heerapura220(RS)-Renwal Ckt tripped during the same time. As reported by SLDC Rajasthan, lines tripped from remote end only on zone-2 protection operation.vi)As per PMU at Bassi(PG), R-Y phase to phase fault was observed with | grid_india_gd/grid_events/2026-06-01
G00333 | 2026-06 | 12 | GI-2 | Haryana | HR | Northern | 2026-06-11T16:35 | 2026-06-11T17:24 | 0.82 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-2 Haryana 11-06-2026 16:35 11-06-2026 17:24 00:49 0 0 0.00% 0.00% 676 74 79732 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole) (as per SCADA). ii)As reported, at 16:35 hrs, 800 KV HVDC Kurukshetra( | 12 GI-2 Haryana 11-06-2026 16:35 11-06-2026 17:24 00:49 0 0 0.00% 0.00% 676 74 79732 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~3000 MW power from Champa to Kurukshetra (~750 MW on each Pole) (as per SCADA). ii)As reported, at 16:35 hrs, 800 KV HVDC Kurukshetra(PG) Pole-2 & 4 tripped on DC line fault with fault distance of 563.814 km from Kurukshetra end (Tower loc. no. 1942). iii)During the same time, 800 KV HVDC Kurukshetra(PG) Pole-3 also got blocked due to instability protection operation. iv)As per PMU at Kurukshetra (PG), no fault was observed in the system; however fluctuation in voltage was observed. v)As per SCADA, no change in demand in Haryana control area was observed. Change in power order of approx 1540 MW occurred during the event. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 3) 800 KV HVDC Kurukshetra(PG) Pole-3 | grid_india_gd/grid_events/2026-06-01
G00334 | 2026-06 | 36 | GD-1 | DDDNH |  |  | 2026-06-11T16:41 | 2026-06-12T00:16 | 7.58 |  | 293 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GD-1 DDDNH 11-06-2026 16:41 12-06-2026 00:16 07:35 - 293 - 0.37% 93169 78 912 Complete outage of 220kV Khadoli (DNHDD): At 16:41 hrs/11.06.2026, 220 kV Kala–Khadoli Circuit-2 tripped due to a broken B-phase jumper at Tower No. 21. Simultaneously 220 kV Kala–Khadoli Circuit-1 also tripped. At the | 11 GD-1 DDDNH 11-06-2026 16:41 12-06-2026 00:16 07:35 - 293 - 0.37% 93169 78 912 Complete outage of 220kV Khadoli (DNHDD): At 16:41 hrs/11.06.2026, 220 kV Kala–Khadoli Circuit-2 tripped due to a broken B-phase jumper at Tower No. 21. Simultaneously 220 kV Kala–Khadoli Circuit-1 also tripped. At the time of the event, both 220 kV Kala–Khadoli double-circuit lines and the 220/66 kV Khadoli ICTs were connected to 220 kV Bus-1 at Khadoli Substation, while the 220 kV Bus Coupler was normally kept open as per the prevailing power regulation scheme. As a result of the tripping of both 220 kV Kala–Khadoli Circuit-1 and Circuit-2, 293 MW load loss was reported. Tripping of following Elements: 1. 220 kV Kala–Khadoli-1&2 | grid_india_gd/grid_events/2026-06-01
G00335 | 2026-06 | 13 | GD-1 | Rajasthan | RJ | Northern | 2026-06-14T09:12 | 2026-06-14T11:41 | 2.48 | 355 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | v)As per PMU at SRI9PL(IP), generation loss of approx 101 MW occurred at Serentica9(IP). | 13 GD-1 Rajasthan 14-06-2026 09:12 14-06-2026 11:41 02:29 355 0 62.83% 0. 00% 56499 60062 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) was generating approx 280 MW (as per SCADA). iii)As reported, at 09:12 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped on differential protection operation from SRI9PL end only (exact nature and location of fault yet to be shared). This led to complete blackout of 400kV Serentica 8 & 9 (IP) S/s. iv)As per PMU at Fatehgarh3(PG), no fault was observed in the system; however sudden change in voltage was observed. v)As per PMU at SRI9PL(IP), generation loss of approx 101 MW occurred at Serentica9(IP). vi)As per SCADA, generation loss of approx 280 MW at Serentica 8 & 9 (IP) and change in NR solar generation of approx 355 MW were observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of June 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/ | grid_india_gd/grid_events/2026-06-01
G00336 | 2026-06 | 37 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-16T17:01 | 2026-06-16T19:15 | 2.23 | 709 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Consequently, a generation loss of 709 MW occurred. | 12 GD-1 Madhya Pradesh 16-06-2026 17:01 16-06-2026 19:15 02:14 709 - 0.75% - 94114 76922 Complete outage of 400 kV Pachora (GR Infra): At 17:01 hrs/ 16.06.2026, an overvoltage condition was observed in the network, originating from the 220 kV Shajapur Line-1 (Unit-7, NTPC_GE) and the 220 kV Agar Line-1 (Unit-4, Avaada). The overvoltage subsequently propagated through the transmission system, resulting in the tripping of following elements- Due to the loss of the evacuation path following the line trippings, all six Renewable Energy (RE) plants connected to Pachora Pooling Station (PS) went offline (became dark). Consequently, a generation loss of 709 MW occurred. Tripping of following Elements: 1. 400kV Pachora-Bhopal Line 1 & 2 2. 220kV Shajapur Line 1(Unit 7, NTPC GE) 3. 220kV Shajapur Line 2(Unit 8, Solar Arise) 4. 220kV Agar Line 1(Unit 4, Avaada Energy) 5. 220kV Agar Line 2(Unit 5, O2 Power) 6. 220kV Malwa_RE (Blueleaf) 7. 220kV VSUPL (Oyster Renewables) | grid_india_gd/grid_events/2026-06-01
G00337 | 2026-06 | 38 | GD-1 | Gujarat | GJ | Western | 2026-06-16T17:56 | 2026-06-16T20:05 | 2.15 | 330 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 330 MW Occurred at GSECL(South Block) Solar plant due to loss of evacuation path. | 13 GD-1 Gujarat 16-06-2026 17:56 16-06-2026 20:05 02:09 330 - 0.35% - 94367 75592 Complete outage of 400 kV GSEC (South Block): At 17:56 hrs / 16-06-2026, 400 kV Khavda PS2-GSECL(South Block)-1 S/C tripped on over voltage protection operation at GSECL(South Block) and DT was sent to Khavda-PS2 end. Generation loss of 330 MW Occurred at GSECL(South Block) Solar plant due to loss of evacuation path. Tripping of following Elements: 1. 400 kV Khavda PS2-GSECL(South Block)-1 S/C | grid_india_gd/grid_events/2026-06-01
G00338 | 2026-06 | 14 | GD-1 | Rajasthan | RJ | Northern | 2026-06-16T21:56 | 2026-06-17T00:58 | 3.03 | 241 | 0 | TRUE | TRUE | FALSE | FALSE | TRUE | vii)As per PMU at ASEJOL(IP) and ASEJOL_wind(IP), generation loss of approx 96 MW occurred at ASEJOL(IP)/ ASEJOL_wind(IP). | 14 GD-1 Rajasthan 16-06-2026 21:56 17-06-2026 00:58 03:02 241 0 37.55% 0. 00% 64184 78802 i)220kV ASEJOL Wind(IP) is connected to 220 kV ASEJOL(IP) through 220kV ASEJOL_HB FTGH2 -ASEJOL_WIND FTGH2 (ASEJOL) Ckt and total generation of 220 kV ASEJOL(IP) and ASEJOL Wind(IP) stations evacuate through 220 KV Fatehgarh_II(PG)-ASEJOL_HB FTGH2 (ASEJOL) (ASEJOL) Ckt-1 & 2. ii)During antecedent condition, ASEJOL(IP) was generating approx 96 MW (as per PMU) which in turn was the generation of ASEJOL Wind(IP) only (non-solar hours). iii)As reported, at 21:56 hrs, 220 KV Fatehgarh_II(PG)-ASEJOL_HB FTGH2 (ASEJOL) (ASEJOL) Ckt-2 tripped on B-N phase to earth fault with fault current of Ib=~0.62 kA and fault distance of 35.7 km from Fathegarh2 end. iv)During the same time, 220 KV Fatehgarh_II(PG)-ASEJOL_HB FTGH2 (ASEJOL) (ASEJOL) Ckt-1 also tripped from ASEJOL end only (exact reason of tripping and nature of protection operation yet to be shared). v)This led to complete blackout out of 220 kV ASEJOL(IP) and 220 kV ASEJOL Wind(IP) S/s. vi)As per PMU at Fatehgarh2(PG), two consecutive B-N phase to earth fault followed by Y-B phase to phase fault followed by Y-N phase to earth fault were observed with fault clearing time of 80 ms, 80 ms, 120 ms and 80 ms respectively. vii)As per PMU at ASEJOL(IP) and ASEJOL_wind(IP), generation loss of approx 96 MW occurred at ASEJOL(IP)/ ASEJOL_wind(IP). viii)As per SCADA, change in Rajasthan wind generation of approx 145 MW was observed. 1) 220 KV Fatehgarh_I | grid_india_gd/grid_events/2026-06-01
G00339 | 2026-06 | 39 | GD-1 | Maharashtra | MH | Western | 2026-06-17T02:03 | 2026-06-17T13:18 | 11.25 | 32 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 40.2 MW Occurred at Manza (POWERICA) due to loss of evacuation path. | 14 GD-1 Maharashtra 17-06-2026 02:03 17-06-2026 13:18 11:15 32 - 0.04% - 83 803 69446 Complete outage of 220 kV Manza (Powerica): At 02:03 hrs / 17-06-2026, 220 kV Jamkhambaliya-Manza-1 S/C tripped on differential protection on Y-E Fault, auto recloser operated at Jamkhambaliya end but line tripped on persistent fault. 3 phase trip issued at Manza end for a fault in single phase (Y-E fault). Insulator flashover at multi circuit tower number AP 02 was identified. Generation loss of 40.2 MW Occurred at Manza (POWERICA) due to loss of evacuation path. Tripping of following Elements: 1. 220 kV Jamkhambaliya-Manza-1 S/C | grid_india_gd/grid_events/2026-06-01
G00340 | 2026-06 | 15 | GD-1 | Rajasthan | RJ | Northern | 2026-06-17T10:37 | 2026-06-17T23:45 | 13.13 | 245 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 220 MW was observed at RSDCL PSS2(IP). | 15 GD-1 Rajasthan 17-06-2026 10:37 17-06-2026 23:45 13:08 245 0 37.98% 0. 00% 64515 72266 i)220kV RSDCL PSS2(IP) is connected at Bhadla2(PG) at 220kV level and its generation evacuates through 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2 _PG (RSDCL) Ckt. ii)During antecedent condition, 220kV RSDCL PSS2(IP) was generating approx 220 MW (as per SCADA). iii)As reported at 10:37 hrs, 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt tripped on O/C E/F protection operation due to issue in CB of Bay No. 202 at RSDCL PSS2 end (exact reason of tripping yet to be shared). iv)Due to tripping of 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt, complete blackout occurred at 220kV RSDCL PSS2(IP). v)As per PMU at Bhadla2(PG), no fault was observed in the system; however sudden change in voltage was observed. vi)As per SCADA, generation loss of approx 220 MW was observed at RSDCL PSS2(IP). 1) 220 KV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt | grid_india_gd/grid_events/2026-06-01
G00341 | 2026-06 | 48 | GD-1 | Sikkim | SK | Eastern | 2026-06-18T02:42 |  |  |  |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of both lines, 220kV Rongnichu HEP became dead and 104 MW generation loss reported at Rongnichu S/s. | 4 GD-1 SIKKIM 18-06-2026 02:42 Still under outage NA 104 0 0.30% 0.00% 34111 31329 Rongnichu Unit-1 & 2 generation was around 104 MW evacuating through 220kV Rangpo Rongnichu D/C line. At 02:42 Hrs on 18/06/2026, 220kV Rangpo- Rongnichu D/C got tripped due to dead end Tower No. 30 from the Rongnichu end got collapsed. Due to tripping of both lines, 220kV Rongnichu HEP became dead and 104 MW generation loss reported at Rongnichu S/s. 220KV-Rongnichu-RANGPO-1 220KV-Rongnichu-RANGPO-2 Rongnichu - UNIT 1 Rongnichu - UNIT 2 5 GI-II SIKKIM 21-06-2026 12:05 21-06-2026 13:52 01:47 106 0 0.42% 0.00% 2 5138 24256 Prior to the disturbance, both generating units of Dikchu HEP (2*48MW) were in service and generating around 106 MW. The generated power was being evacuated through 400/132kV ICT and 400kV Main Bus 2( 400kV Rangpo line- 2 was under outage condition. At 12:05 Hrs on 21.06.2026, 400/132kV ICT got tripped due to master trip relay operation (Master trip signal extended by SF6 gas density monitor of outdoor GIS compartment unit), resulting in loss of evacuation path of Dikchu Unit-1 & 2. Total generation loss of 106 MW reported at Dikchu HEP. 400/132kV ICT at Dikchu 48 MW U#1 at Dikchu 48 MW U#2 at Dikchu 6 GI-II SIKKIM 22-06-2026 07:20 22-06-2026 10:49 03:29 106 0 0.31% 0.00% 3 4298 24256 Prior to the disturbance, both generating units of Dikchu HEP (2*48MW) were in service and generating around 106 MW. Generated power was evacuated through 400/132kV ICT and 400kV Main Bus 2( 400k | grid_india_gd/grid_events/2026-06-01
G00342 | 2026-06 | 40 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-18T11:49 | 2026-06-18T12:59 | 1.17 | 100 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 100 MW occurred at U6. | 15 GD-1 Madhya Pradesh 18-06-2026 11:49 18-06-2026 12:59 01:10 100 - 0.12% - 85807 72328 Complete outage of 220 kV Shajapur Unit-6 (Burley): At 11:49 Hrs/18.06.2026, 220 kV Shajapur Unit-6 (Burley) - Shajapur Unit-7 (Dehripal) line tripped on Y-B fault. Due to the loss of evacuation path, 220 kV Shajapur Unit-6 (Burley) Solar Power Plant became dark. Generation loss of 100 MW occurred at U6. Tripping of following Elements: 1. 220 kV Shajapur Unit-6 (Burley) - Shajapur Unit-7 (Dehripal) | grid_india_gd/grid_events/2026-06-01
G00343 | 2026-06 | 41 | GD-1 | Madhya Pradesh | MP | Western | 2026-06-18T11:49 | 2026-06-18T13:59 | 2.17 | 340 |  | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 340 MW occurred. | 16 GD-1 Madhya Pradesh 18-06-2026 11:49 18-06-2026 13:59 02:10 340 - 0.40% - 85807 72328 Complete outage of 220 kV Agar (Umariah): At 11:49 Hrs, 220 kV Umariya (Agar Unit-5)-Pachora line tripped on Y-G fault. Due to the loss of evacuation path, 220 kV Umariya Agar Unit-5 Solar Power Plant became dark. Generation loss of 340 MW occurred. All elements restored by 14:08Hrs. Tripping of following Elements: 1. 220 kV Umariya (Agar Unit-5)-Pachora Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 TAMILNADU , KERALA 02-06-2026 06:37 02-06-2026 07:45 01:08 168 0 0.38% 0.00% 43939.75 5241 6.46 Complete outage of 220kV Sabarigiri PH of KSEB As per the reports submitted, the triggering incident was failure of the R-phase pole of the Generator Main Circuit Breaker of Unit-5 to open during a normal shutdown of the generating unit leading to operation of the Local Breaker Backup (LBB) protection and further due to an isolator discrepancy associated with Unit- 5, both the 220 kV Main Bus and 220 kV Transfer Bus were tripped leading to the Complete outage of 220kV Sabarigiri PH of KSEB. 220KV-EDAMON-SABARIGIRI-3, 220KV-EDAMON- SABARIGIRI-1, 220KV-EDAMON-SABARIGIRI-2, 220KV- SABARIGIRI-PALLOM-1, 220KV-THENI-SABARIGIRI-1, 220KV- AMBALAMUGAL-SABARIGIRI-1 2 GD - 1 TAMILNADU 03-06-2026 18:34 03-06-2026 20:14 01:40 483 0 1.01% 0. 00% 47757.12 52430.01 Complete Outag | grid_india_gd/grid_events/2026-06-01
G00344 | 2026-06 | 16 | GD-1 | Punjab | PB | Northern | 2026-06-18T13:29 | 2026-06-18T14:10 | 0.68 | 0 | 775 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GD-1 Punjab 18-06-2026 13:29 18-06-2026 14:10 00:41 0 775 0.00% 96.11% 73045 80638 i)220kV Wadala Granthian(PS) has double main bus scheme at 220kV level. 220kV Wadala Granthian(PS) has supply from Sarna through two direct lines and two lines via Gurdaspur and Tibber. 220kV Wadala Granthian(PS) a | 16 GD-1 Punjab 18-06-2026 13:29 18-06-2026 14:10 00:41 0 775 0.00% 96.11% 73045 80638 i)220kV Wadala Granthian(PS) has double main bus scheme at 220kV level. 220kV Wadala Granthian(PS) has supply from Sarna through two direct lines and two lines via Gurdaspur and Tibber. 220kV Wadala Granthian(PS) also has supply from 400kV Bala Chakk through 220kV Verpal-Bala Chakk D/C which are further connected through one direct line from Verpal and other line via Udhoke to Wadala Granthian.ii)During antecedent condition, 220kV Civil Lines-Chogawan Ckt and 220kV Civil Lines-Khaasa Ckt were out of service since 13:00 hrs. 220kV Verpal-Bala Chakk Ckt-2 was also under tripped condition since 11:27 hrs due to snapping of Y-Ph conductor between tower span no. 2 & 3 (Y-B phase to phase fault sensed in zone-1 at Verpal end, fault current of Iy =6.65 kA, Ib=6.302 kA and fault distance of 206.9 m from Verpal). After tripping of 220kV Verpal-Bala Chakk Ckt-2, 220kV Verpal-Udhoke Ckt and 220kV Verpal-Wadala Granthian Ckt were opened to manage loading on 220kV Verpal-Bala Chakk Ckt-1. Hence, 220kV Wadala Granthian(PS) had left with only supply from Sarna through two direct lines and two lines via Gurdaspur and Tibber. 220kV Kotli Surat Malhi, Fatehgarh Churian, Majitha, Udhoke & Civil Lines were being fed radially from 220kV Wadala Granthian(PS).iii)As reported, at 13:21 hrs, 220kV Sarna-Wadala (PS) Ckt-1 tripped on R-N phase to earth fault wit h fault current of 2.263 kA & fault distance of 57.46 km | grid_india_gd/grid_events/2026-06-01
G00345 | 2026-06 | 17 | GD-1 | Uttar Pradesh | UP | Northern | 2026-06-18T19:23 | 2026-06-18T20:49 | 1.43 | 2290 | 530 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GD-1 Uttar Pradesh 18-06-2026 19:23 18-06-2026 20:49 01:26 2290 530 3 09.87% 70.43% 73903 75253 i)During antecedent condition, 500MW Unit-1, 2, 3, 4 & 5 at Rihand complex were running and generating total ~2300 MW. HVDC Rihand-Dadri were carrying ~1350 MW total. ii)As reported, at 13:29:31:520 hr | 17 GD-1 Uttar Pradesh 18-06-2026 19:23 18-06-2026 20:49 01:26 2290 530 3 09.87% 70.43% 73903 75253 i)During antecedent condition, 500MW Unit-1, 2, 3, 4 & 5 at Rihand complex were running and generating total ~2300 MW. HVDC Rihand-Dadri were carrying ~1350 MW total. ii)As reported, at 13:29:31:520 hrs, Y-N fault occurred near to the gantry of Rihand(NTPC) switchyard. During inspection of associated equipme nt in the Gantry area, few strands of HVDC AC line-2 Y-phase (dropper conductor from Jack bus to 400 KV BUS side Isolator) were found damaged.iii)The Main-II relay at Singrauli end of 400kV Singrauli-Rihand line-II sensed the fault in Z-1 and initiated Y- Ph A/R. The same fault was sensed by Rihand end in Z-4. iv)The same fault was sensed by all other lines i.e., 400kV Rihand-Singrauli Line-1 and 400kV Rihand-Allahabad D/C in Z-4 by Rihand end and Z-2 by remote end distance protection. Within ~350msec, 400kV Rihand-Singrauli Line-1 tripped and in ~560msec 400kV Rihand-Allahabad D/C tripped from remote end in Z-2.v)As per PMU at Singrauli(NTPC), Allahabad(PG) and Rihand(NTPC), Y-N fault converted into three phase fault is observed. It was als o observed that all the 400kV lines tripped within 650msec and voltage at 400kV Bus at Rihand got dead by 2sec delay. vi)After tripping of above lines, loading of R & B phase of 400kV Singrauli-Rihand line-II increased and power swing detected. In ~800msec of y-ph A/R start, line tripped on distance protection operation from both ends du | grid_india_gd/grid_events/2026-06-01
G00346 | 2026-06 | 18 | GI-2 | Haryana | HR | Northern | 2026-06-19T12:01 | 2026-06-19T13:00 | 0.98 | 0 | 265 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GI-2 Haryana 19-06-2026 12:01 19-06-2026 13:00 00:59 0 265 0.00% 33.14 % 72753 79975 i)220KV Samaypur(BBMB) has double main bus scheme. There are 03 (three) 220kV Buses i.e., Bus-1, Bus-2A and Bus-2B. 400/220kV 500 MVA ICT-1,2,3&4 at Ballabhgarh(PG) feeds the 220kV Samaypur S/s. ii)During the ant | 18 GI-2 Haryana 19-06-2026 12:01 19-06-2026 13:00 00:59 0 265 0.00% 33.14 % 72753 79975 i)220KV Samaypur(BBMB) has double main bus scheme. There are 03 (three) 220kV Buses i.e., Bus-1, Bus-2A and Bus-2B. 400/220kV 500 MVA ICT-1,2,3&4 at Ballabhgarh(PG) feeds the 220kV Samaypur S/s. ii)During the antecedent condition, 400/220kV 500 MVA ICT-4 at Ballabhgarh(PG) was under shut down. iii)As reported, at 12:01 hrs, LBB protection of 400/220kV 500 MVA ICT-3 at Ballabhgarh(PG) (220kV Samaypur side) mal-operated during testing work of 400/220kV 500 MVA ICT-4 at Ballabhgarh(PG) due to wiring issue at 220kV Samaypur(BB). iv)Due to LBB protection operation, 220kV Samaypur- Ballabhgarh (BB) Ckt-1 & 3, 220kV Samaypur(BB)- Palli(HV) (HVPNL) Ckt-1, 220kV Samaypur(BB)- Badshahpur(HV) (HVPNL) Ckt-1, 220kV Faridabad Sec58(HV)- Samaypur(BB) (HVPNL) Ckt-2 and 400/220kV 500 MVA ICT-2 & 3 at Ballabhgarh(PG) tripped. v)As per PMU at Ballabhgarh(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 265 MW in Haryana control area was observed. vii)As informed by BBMB, wiring issue at 220kV Samaypur(BB) is now resolved. 1) 400/220kV 500 MVA ICT-2 at Ballabhgarh(PG) 2) 400/220kV 500 MVA ICT-3 at Ballabhgarh(PG) 3) 220kV Samaypur- Ballabhgarh (BB) Ckt-1 4) 220kV Samaypur- Ballabhgarh (BB) Ckt-3 5) 220kV Samaypur(BB)- Palli(HV) (HVPNL) Ckt-1 6) 220kV Samaypur(BB)- Badshahpur(HV) (HVPNL) Ckt-1 7) 220kV Faridabad Sec58(HV)- Samaypur(BB) (HVPNL) Ckt-2 | grid_india_gd/grid_events/2026-06-01
G00347 | 2026-06 | 45 | GI-1 | Andhra Pradesh | AP | Southern | 2026-06-21T05:05 | 2026-06-21T05:39 | 0.57 | 620 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GI-1 ANDHRA PRADESH 21-06-2026 05:05 21-06-2026 05:39 00:34 620 0 1.33% 0.00% 46568.5 49428 .06 Tripping of 220kV Bus-2 of VTPS Generating station of APGENCO As per the reports submitted, the triggering incident was R-G fault in 220kV VTPS CHillakallu Line-1. At VTPS end, though the breaker opene | 18 GI-1 ANDHRA PRADESH 21-06-2026 05:05 21-06-2026 05:39 00:34 620 0 1.33% 0.00% 46568.5 49428 .06 Tripping of 220kV Bus-2 of VTPS Generating station of APGENCO As per the reports submitted, the triggering incident was R-G fault in 220kV VTPS CHillakallu Line-1. At VTPS end, though the breaker opened, the current interference in the R-phase chamber got delayed causing 220kV LBB to operate. Immedeately all elements connected to 220kV Bus-2 tripped at 220kV VTPS Generating station. 220KV-VTPS-CHILLAKALLU-2, 220KV-VTPS- RENTACHINTHALA-2, 220KV-TADIKONDA-VTPS-2, 220KV- GUNADALA-VTPS-2, 220KV-VTPS-NARSARAOPET-1, 220KV- VTPS-NUZVID-1, 220KV-KONDAPALLI-VTPS-2, 220KV-VTPS- PIDUGURALLA-2, VTPS - 220KV - Bus 2 | grid_india_gd/grid_events/2026-06-01
G00348 | 2026-06 | 19 | GI-2 | Himachal Pradesh | HP | Northern | 2026-06-24T14:36 | 2026-06-24T15:44 | 1.13 | 127 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 127 MW was observed at Parbati-3(NH). | 19 GI-2 Himachal Pradesh 24-06-2026 14:36 24-06-2026 15:44 01:08 127 0 20.68% 0.00% 61423 66804 i)During antecedent condition, 130 MW Parbati III HEP - UNIT 2 was in running condition and generating approx 127 MW (as per SCADA). ii)As reported, at 14:36 hrs, 400 KV Parbati_3(NH)-Parbati Pooling Banala(PG) (PKTCL) Ckt tripped on B-N phase to earth fault with fault distance of 12.73 km from Banala end & 3.4 km from Parbati-3 end and fault current of 4.8 kA from Banala end & 3.8 kA from Parbati-3 end iii)During the same time, 400 KV Parbati_3(NH)-Sainj(HP) (PKTCL) Ckt auto-reclosed from Parbati-3 end (exact reason of auto-recloser yet to be shared). iv)Due to momentary loss of evacuation path, 130 MW PARBATI III HEP - UNIT 2 tripped. v)As per PMU at Banala(PG), B-N phase to earth fault was observed with fault clearing time of 80 ms. vi)As per SCADA, generation loss of approx 127 MW was observed at Parbati-3(NH). 1) 400 KV Parbati_3(NH)-Parbati Pooling Banala(PG) (PKTCL) Ckt 2) 130 MW Parbati III HEP - UNIT 2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of June 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Anteceden | grid_india_gd/grid_events/2026-06-01
G00349 | 2026-06 | 49 | GD-1 | Bihar | BR | Eastern | 2026-06-26T14:52 | 2026-06-26T15:21 | 0.48 | 0 | 110 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GD-1 BIHAR 26-06-2026 14:52 26-06-2026 15:21 00:29 0 110 0.00% 0.37% 292 33 30010 At 14:52 Hrs on 26/06/2026, B-Phase CT of 220kV-Biharsharif (BH)- Tenughat line at Biharsharif (BH) got burst with heavy spark and created a bus fault. All 400/220kV ICTs at Biharsarif (BH) got tripped on high set over current earth fault protection and all 220kV lines tripped on Z-4 protection from Biharsarif(BH) end. 220kV Biharsarif(BH) S/s became dead. Total load loss of 110 MW reported at Biharsarif S/s. 220KV-BIHARSARIF-TTPS-1 220KV-BIHARSARIF-MOKAMA-1 220KV-BIHARSARIF-MOKAMA-2 400KV/220KV 315 MVA ICT 1 AT BIHARSARIF(PG) 400KV/220KV 315 MVA ICT 2 AT BIHARSARIF(PG) 400KV/220KV 315 MVA ICT 3 AT BIHARSARIF(PG) 400KV/220KV 500 MVA ICT 4 AT BIHARSARIF(PG) 220KV-BIHARSARIF-Khizersarai-1 220KV-BIHARSARIF-Khizersarai-2 220KV-BIHARSARIF-Fatuha-1 220KV-BIHARSARIF-Fatuha-2 220/132KV 160MVA ICT1 at Biharsharif(BH) 220/132KV 160MVA ICT2 at Biharsharif(BH) 220/132KV 160MVA ICT3 at Biharsharif(BH) Elements Tripped Details of Grid Events during the Month of June 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI | grid_india_gd/grid_events/2026-06-01
G00350 | 2026-06 | 20 | GI-1 | Haryana | HR | Northern | 2026-06-26T16:24 | 2026-06-26T19:55 | 3.52 | 0 | 455 | FALSE | FALSE | FALSE | FALSE | FALSE | 20 GI-1 Haryana 26-06-2026 16:24 26-06-2026 19:55 03:31 0 455 0.00% 54.12% 72190 84077 i)220/66KV Palli(HVPNL) Sub-station has double main bus system at both 220kV and 66kV level. ii)As reported, at 16:24 hrs, 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 & 2 tripped (exact reason of fault yet to be s | 20 GI-1 Haryana 26-06-2026 16:24 26-06-2026 19:55 03:31 0 455 0.00% 54.12% 72190 84077 i)220/66KV Palli(HVPNL) Sub-station has double main bus system at both 220kV and 66kV level. ii)As reported, at 16:24 hrs, 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 & 2 tripped (exact reason of fault yet to be shared). iii)As per EL at Samaypur end of 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-2, line tripped on Y-B phase to phase fault with fault distance of 25.47 km and fault current of Iy=~6.1kA, Ib=~4.876kA from Samaypur . Fault sensed in zone-3 at Samypur end and fault duration was 105.1 ms.iv)As per EL at Samaypur end of 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1, line tripped on R-Y phase to phase fault with fault distance of 13.98 km and fault current of Ir=~8.369kA, Iy=~8.222kA from Samaypur . Fault sensed in zone-2 at Samypur end and fault duration was 877.5 ms (delayed clearance).v)As per PMU at Ballabhgarh(PG), Y-B phase to phase fault followed by R-Y phase to phase fault was observed with fault clearing time of 80 ms and 920 ms (delayed) respectively.vi)As per SCADA, change in demand of approx 455 MW was observed in Haryana control area. 1) 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 2) 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-2 | grid_india_gd/grid_events/2026-06-01
G00351 | 2026-06 | 46 | GI-2 | TAMILNADU |  |  | 2026-06-26T19:22 | 2026-06-26T23:34 | 4.2 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | 19 GI-2 TAMILNADU 26-06-2026 19:22 26-06-2026 23:34 04:12 0 0 0.00% 0.00% 5 2953.73 55359.88 Tripping of 400kV Bus-2 of 400kV Alamathy SS of TANTRANSCO The triggering incident is the tripping of 400 kV Bus-2 at 400 kV Alamathy Substation due to the operation of 400kV Bus-2 BBP with no fault during the event. This led to tripping of all main breakers connected to 400kV Alamathy Bus-2. Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-06-01
G00352 | 2026-06 | 21 | GI-2 | Himachal Pradesh | HP | Northern | 2026-06-27T09:20 | 2026-06-27T09:34 | 0.23 | 860 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 172 MW at Rampur HEP, 363 MW at Nathpa Jhakri HPS, 302 MW at Karcham Wangtoo HPS, and 23 MW at Naitwar Mori HEP (total 860 MW) were observed. | 21 GI-2 Himachal Pradesh 27-06-2026 09:20 27-06-2026 09:34 00:14 860 0 114.11% 0.00% 75365 81150 i)During antecedent condition, 37 MW Unit-1, 2 & 3 at Sawra Kuddu HEP were not in service. 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-1 & 2 were carrying approx. 710 MW each (as per PMU). ii)As reported, at 09:20 hrs, 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-2 first successfully auto-reclosed on R-N phase to earth fault, but finally tripped on another R-N phase to earth fault within reclaim time with fault distance of 12.19 km and fault current of 10.22kA from Nallagarh(PG) end. iii)Due to tripping of 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-2, loading of 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-1 exceeded 900 MW and reached upto 1008 MW (as per PMU). iv)Due to this, SPS (Case-1) at N. Jhakri, Rampur, Karcham generation complex operated and one unit each at Nathpa Jhakri, Karcham Wangtoo and Naitwar Mori HEP and two units at Rampur HEP tripped (as per logic, only one unit should have tripped at Rampur HEP; Rampur is requested to share reason of tripping of two units instead of one as per logic). v)As per PMU, R-N phase to earth fault with successful A/R followed by another R-N phase to earth fault within reclaim time was observed. vi)As per SCADA, generation loss of approx 172 MW at Rampur HEP, 363 MW at Nathpa Jhakri HPS, 302 MW at Karcham Wangtoo HPS, and 23 MW at Naitwar Mori HEP (total 860 MW) were observed. 1) 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-2 2) 68.67 M | grid_india_gd/grid_events/2026-06-01
G00353 | 2026-06 | 22 | GD-1 | Uttar Pradesh | UP | Northern | 2026-06-27T17:31 | 2026-06-27T18:25 | 0.9 | 0 | 510 | FALSE | FALSE | FALSE | FALSE | FALSE | 22 GD-1 Uttar Pradesh 27-06-2026 17:31 27-06-2026 18:25 00:54 0 510 0.00 % 59.73% 69403 85379 i)765/400/220KV Unnao(UP) has one and half breaker scheme at 765KV level and double main & transfer bus scheme at 400KV & 220kV level. ii)During antecedent condition, 400kV Bareilly-Unnao D/C were under out | 22 GD-1 Uttar Pradesh 27-06-2026 17:31 27-06-2026 18:25 00:54 0 510 0.00 % 59.73% 69403 85379 i)765/400/220KV Unnao(UP) has one and half breaker scheme at 765KV level and double main & transfer bus scheme at 400KV & 220kV level. ii)During antecedent condition, 400kV Bareilly-Unnao D/C were under outage since 25.05.2026 due to tower collapse, 400kV Agra(PG)-Unnao(UP) line was under emergency shutdown since 13:22 hrs of same day and 400/220kV 500 MVA ICT-1 at Unnao(UP) was also under outage since 21.04.2026. MW loading of 765/400 kV 1000 MVA ICT 1, 2 & 3 at Unnao(UP) and 400/220 kV 500 MVA ICT 2 & 315 MVA ICT-3 at Unnao(UP) were 480 MW, 481 MW, 498 MW, 259 MW & 176 MW respectively.iii)As reported, at 17:31 hrs, bus bar protection of 400kV Bus-1 & 2 operated resulted in tripping of all the elements i.e., 765/400 kV 1000 MVA ICT 1, 2 & 3 at Unnao(UP), 400/220 kV 500 MVA ICT 2 & 315 MVA ICT-3 at Unnao(UP), 400 KV Unnao(UP)-Jehta_Hardoi Road (UP) (PG) D/C, 400 KV Unnao-Panki (UP) Ckt-1 and 400 KV Mohanlalganj (PGYTL)-Unnao(UP) (PGYTL) Ckt-1. Fault occurred due to bird collision. (Further details of fault yet to be received).iv)As per PMU at Bareilly(PG), R-N phase to earth fault which cleared within 100msec is observed. v)As per SCADA, change in demand of ~510 MW is observed in UP control area. vi)As reported, power supply to 220kV Bithoor(UP), 220kV Phoolbagh(UP), 220kV Dahichowki(UP), 220kV RPH(UP), 132kV Sonik(UP) and 132kV Maurawan(UP) affected during the event. vii)Exact reaso | grid_india_gd/grid_events/2026-06-01
G00354 | 2026-06 | 23 | GD-1 | Rajasthan | RJ | Northern | 2026-06-28T09:11 | 2026-06-28T11:19 | 2.13 | 742 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | viii)As per SCADA change in NR total Solar generation of approx 580 MW was observedSolar Generation loss of approx 742 MW [182 MW at RSVPL(IP) 244 MW at 1) 220 KV RSVPL_SL_FTHG3_PG-Fatehgarh_III(PG) (RENEW SURYA VIHAAN PRIVATE LIMITED) Ckt 2) 220 KV Fatehgarh_III(PG)-RSRPL_Hyb_FTHG3_PG (RENEW SURYA ROSHNI PRIVATE LIMITED) Ckt 3) 400 KV FATEHGARH_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt | 23 GD-1 Rajasthan 28-06-2026 09:11 28-06-2026 11:19 02:08 742 0 103.97% 0 .00% 71366 78052 i)220kV Renew Saurya Vihan (IP) is connected to 220 kV Renew Saurya Pratap (IP) through 220kV Ckt and total generation of 220 kV Renew Saurya Vihan (IP) and Renew Saurya Pratap(IP) stations, i.e., RSVPL(IP) evacuate through 220kV RSVPL_SL_FTHG3_PG-Fatehgarh_III(PG) (RENEW SURYA VIHAAN PRIVATE LIMITED) Ckt. 220kV Renew Roshni (IP) is connected to 220 kV Fatehgarh 3 pooling station and generation of this plant evacuates through 220 kV Fatehgarh_III(PG)-RSRPL_Hyb_FTHG3_PG (RENEW SURYA ROSHNI PRIVATE LIMITED) Ckt. 400kV SRI8PL (IP) is connected to 400 kV SRI9PL (IP) through 400kV Ckt and total generation of SRI8PL (IP) and SRI9PL (IP) stations evacuate through 400kV FATEHGARH_III(PG)-SRI9PL_SL_FTG3 (Serentica_RI9PL) Ckt. ii)During antecedent condition, RSVPL(IP) was generating total 182 MW [Renew Saurya Pratap(IP) and Renew Saurya Vihan(IP) were generating approx 124 MW and 58 MW respectively], Renew Roshni (IP) was generating approx 244 MW and SRI8&9PL(IP) was generating approx 316 MW (as per SCADA). iii)As reported, at 09:11 hrs, 220 KV Fatehgarh_III(PG)-RSRPL_Hyb_FTHG3_PG (RENEW SURYA ROSHNI PRIVATE LIMITED) Ckt-1 tripped on B-N phase to earth fault (exact nature and location of fault and nature of protection operation yet to be shared) due to B phase jumper broken. iv)220 KV RSVPL_SL_FTHG3_PG-Fatehgarh_III(PG) (RENEW SURYA VIHAAN PRIVATE LIMITED) Ckt also tripped at the same time as the | grid_india_gd/grid_events/2026-06-01
G00355 | 2026-06 | 24 | GI-2 | Uttar Pradesh | UP | Northern | 2026-06-29T00:22 | 2026-06-29T00:57 | 0.58 | 0 | 246 | FALSE | FALSE | FALSE | FALSE | FALSE | 24 GI-2 Uttar Pradesh 29-06-2026 00:22 29-06-2026 00:57 00:35 0 246 0.00% 27.28% 64882 90179 i)400/220KV Agra(UP) has double main & transfer bus scheme at 400KV & 220kV level. ii)As reported, at 00:22 hrs, 220kV Agra-Hathras(UP) Ckt tripped on B-N phase to earth fault with fault distance of 4.767 km | 24 GI-2 Uttar Pradesh 29-06-2026 00:22 29-06-2026 00:57 00:35 0 246 0.00% 27.28% 64882 90179 i)400/220KV Agra(UP) has double main & transfer bus scheme at 400KV & 220kV level. ii)As reported, at 00:22 hrs, 220kV Agra-Hathras(UP) Ckt tripped on B-N phase to earth fault with fault distance of 4.767 km and fault current of 14.22kA from Agra(UP); fault sensed in zone-1 at Agra(UP). iii)Due to delayed clearance of fault, LBB of 220kV Bus-2 at Agra(UP) operated resulting in tripping of all the elements connected to Bus-2. iv)Further, as reported, 220/132kV 160 MVA ICT-3 at Agra(UP) (connected to 220kV Bus-1) also tripped at the same time on backup overcurrent protection operation (exact reason of tripping yet to be shared). v)As per SCADA SOE, 220kV Agra-Agra220(UP) Ckt-2 also tripped during the same time (exact reason of tripping and nature of protection operation yet to be shared). vi)As per PMU at Agra(PG), B-N phase to earth fault was observed with fault clearing time of 80 ms. vii)As per SCADA, change in demand of approx 246 MW was observed in UP control area. 1) 220kV Agra-Hathras(UP) Ckt 2) 220kV Agra-Gokul(UP) Ckt 3) 220kV Agra-IOCL (UP) Ckt-1 4) 220kV Agra-IOCL (UP) Ckt-2 5) 400/220kV 500 MVA ICT-1 at Agra(UP) 6) 220/132kV 160 MVA ICT-4 at Agra(UP) 7) 220/132kV 160 MVA ICT-3 at Agra(UP) | grid_india_gd/grid_events/2026-06-01
G00356 | 2026-06 | 25 | GI-1 | Rajasthan | RJ | Northern | 2026-06-30T03:24 | 2026-06-30T15:10 | 11.77 | 1290 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | v)As per SCADA, Rajasthan Wind generation loss of approx 1290 MW at 03:24 hrs and 1065 MW at 04:14 hrs were observed. | 25 GI-1 Rajasthan 30-06-2026 03:24 30-06-2026 15:10 11:46 1290 0 200.64% 0 .00% 64295 88615 i)During antecedent condition, active power flow in 220kV Akal(RS)-SHEO Ckt was 75 MW. ii)As reported, at 03:24 hrs, 220kV Akal(RS)-SHEO Ckt tripped on Y-N phase to earth fault (R-N phase to earth fault as per PMU) with fault distance of 89.91km and fault current of 1.213kA from SHEP end; fault sensed in zone-2 at SHEO end. iii)During charging aƩempt of 220kV Akal(RS)-SHEO Ckt at 04:14 hrs, line did not hold due to persistent fault in line. Upon investigation, jumper was found snapped at loc no. 1 at Akal(RS) end. iv)As per PMU at Bhadla(PG), R-N phase to earth fault at 03:24 hrs and two consecutive R-N phase to earth faults at 04:14 hrs were observed with fault clearing time of 80 ms each. v)As per SCADA, Rajasthan Wind generation loss of approx 1290 MW at 03:24 hrs and 1065 MW at 04:14 hrs were observed. 1) 220kV Akal(RS)-SHEO Ckt Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-06-01
G00357 | 2026-07 | 20 | GI-1 | DNH |  |  | 2026-07-01T16:03 | 2026-07-01T17:10 | 1.12 | 58 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-1 DNH 01-07-2026 16:03 01-07-2026 17:10 01:07 58 - 0.09% - 63738 54790 Complete outage of 220 kV New Kharadpada S/S: At around 16:03–16:04 hrs on 03-07-2026, during heavy rainfall, moisture ingress into the B-phase pole control unit auxiliary relay of the 220 kV Kala – New Kharadpada Ckt-1 circ | 1 GI-1 DNH 01-07-2026 16:03 01-07-2026 17:10 01:07 58 - 0.09% - 63738 54790 Complete outage of 220 kV New Kharadpada S/S: At around 16:03–16:04 hrs on 03-07-2026, during heavy rainfall, moisture ingress into the B-phase pole control unit auxiliary relay of the 220 kV Kala – New Kharadpada Ckt-1 circuit breaker (Alstom make) at New Kharadpada S/S caused spurious tripping of B-phase pole, followed by tripping of other two poles. It was reported that frequent close/open commands were being given to that breaker due to faulty auxiliary unit. The 220 kV Bus couplor-1 interpreted this as a Local Breaker Backup (LBB) condition and all breakers connected to 220 kV Bus-1 i.e. the 220 kV Kharadpada – New Kharadpada Ckt-1 , 220 kV RIL-1 and 220 kV Kala1 tripped. One 125 MVA RIL Industries transformer fed through RIL Ckt-1 was isolated. Since the second 125 MVA transformer at RIL was running with its LV side paralleled, the associated load of approximately 58 MW dropped to zero. Tripping of following Elements: 1. 220 kV Kala – New Kharadpada Ckt-1 | grid_india_gd/grid_events/2026-07-01
G00358 | 2026-07 | 21 | GD-1 | Gujarat | GJ | Western | 2026-07-03T17:58 | 2026-07-04T03:07 | 9.15 | 73 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 73MW reported due to loss of evacuation path. | 2 GD-1 Gujarat 03-07-2026 17:58 04-07-2026 03:07 09:09 73 - 0.09% - 81786 65088 Complete outage of 220 kV Khakharda S/S: At 17:58 Hrs/03-07-2026, 220KV Jamkhambaliya-Khakharda line tripped due to B- phase to Earth fault (faulty insulator at Tower-145). Generation loss of 73MW reported due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220KV Jamkhambaliya-Khakharda | grid_india_gd/grid_events/2026-07-01
G00359 | 2026-07 | 1 | GD-1 | Rajasthan | RJ | Northern | 2026-07-04T17:13 | 2026-07-04T22:37 | 5.4 | 91 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | x)Total solar generation loss of 91 MW occurred [approx 35MW at ASEB1L(IP) (as per SCADA), 11 MW at RSVPL(IP) (as reported by plant), 9 MW at RSJPL(IP) (as reported by plant) and 36 MW at SRI8&9PL(IP) (as reported by plant)]. | 1 GD-1 Rajasthan 04-07-2026 17:13 04-07-2026 22:37 05:24 91 0 0.14 0.00 64912 81595 i)220kV ASEB1L (IP) is connected to 220 kV Fatehgarh 3 pooling station and generation of this plant evacuates through 220 KV Fatehgarh_III(PG)-ASEB1L_SL_FTG3 (ASEB1L) Ckt-1 and Ckt-2. 220kV Renew Saurya Vihan (IP) is connected to 220 kV Renew Saurya Pratap (IP) through 220kV Ckt and total generation of 220 kV Renew Saurya Vihan (IP) and Renew Saurya Pratap(IP) stations, i.e., RSVPL(IP) evacuate through 220kV RSVPL_SL_FTHG3_PG- Fatehgarh_III(PG) (RENEW SURYA VIHAAN PRIVATE LIMITED) Ckt. 220kV Renew Jyoti (IP) is connected to 220 kV Fatehgarh 3 pooling station and generation of this plant evacuates through 220 KV Fatehgarh_III(PG)- RSJPL_SL_Ftg3(PG) (ReNew_SJPL) Ckt-1. 400kV SRI8PL (IP) is connected to 400 kV SRI9PL (IP) through 400kV Ckt and total generation of SRI8PL (IP) and SRI9PL (IP) stations evacuate through 400kV FATEHGARH_III(PG)- SRI9PL_SL_FTG3 (Serentica_RI9PL) Ckt. ii)During antecedent condition, ASEB1L(IP) was generating approx 35MW (as per SCADA), RSVPL(IP) was generating total 11 MW (as reported by plant), Renew Jyoti (IP) was generating approx 9 MW (as reported by plant) and SRI8&9PL(IP) was generating approx 36 MW (as reported by plant). iii)As reported, at 17:13 hrs, 220 KV Fatehgarh_III(PG)-ASEB1L_SL_FTG3 (ASEB1L) Ckt-1 tripped on R-N phase to earth fault; fault was sensed in zone 1 from both ends with fault current of 17.5kA from PG end and 2.2kA from ASEB1L end; fault distan | grid_india_gd/grid_events/2026-07-01
G00360 | 2026-07 | 22 | GD-1 | Madhya Pradesh | MP | Western | 2026-07-05T11:43 | 2026-07-05T12:58 | 1.25 | 505 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 505 MW Occurred at MB Power (HINDUSTAN POWER) due to loss of evacuation path. | 3 GD-1 Madhya Pradesh 05-07-2026 11:43 05-07-2026 12:58 01:15 505 - 0.77% - 65462 55798 Complete outage of 400kV MB Power S/S: At 11:43 hrs / 05-07-2026, 400 kV Jabalpur-MB Power-1 tripped on Y-E Fault. Auto recloser was out of service in 400 kV Jabalpur-MB Power-1 from 09:33 hrs due to planned shutdown 400 kV Jabalpur-MB Power-2 for LBB relay testing at Jabalpur end (Outage availed by Powergrid WR-2). Generation loss of 505 MW Occurred at MB Power (HINDUSTAN POWER) due to loss of evacuation path. Since Both lines from MB Power tripped GD occurred. Tripping of following Elements: 1. 400 kV Jabalpur-MB Power-1 | grid_india_gd/grid_events/2026-07-01
G00361 | 2026-07 | 56 | GI-2 | Karnataka | KA | Southern | 2026-07-05T12:03 | 2026-07-05T12:32 | 0.48 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-2 KARNATAKA 05-07-2026 12:03 05-07-2026 12:32 00:29 0 0 0.00% 0.00% 52743.59 47729.89 Tripping of 400kV Bus-2 at Devanahalli of KPTCL As per the reports submitted, 400/220kV ICT-2 was under maintenance for relay calibration. During calibration and current injection differential relay protectio | 11 GI-2 KARNATAKA 05-07-2026 12:03 05-07-2026 12:32 00:29 0 0 0.00% 0.00% 52743.59 47729.89 Tripping of 400kV Bus-2 at Devanahalli of KPTCL As per the reports submitted, 400/220kV ICT-2 was under maintenance for relay calibration. During calibration and current injection differential relay protection operated and since the current was persisting, LBB operated and tripped all the main breakers connected to Bus-2 and tie breaker of ICT-3 leading to the Tripping of 400kV Bus-2 at Devanahalli of KPTCL and 400/220kV ICT-3 at Devanahalli. 400KV/220KV DEVANAHALLI-ICT-3, DEVANAHALLI - 400KV - Bus 2 | grid_india_gd/grid_events/2026-07-01
G00362 | 2026-07 | 57 | GI-1 | Kerala | KL | Southern | 2026-07-05T17:00 | 2026-07-05T18:20 | 1.33 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-1 KERALA 05-07-2026 17:00 05-07-2026 18:20 01:20 0 0 0.00% 0.00% 48525.17 44394.28 Tripping of 220kV Bus-1 & Bus-3 of 220kV Pothencode SS of KSEB As per the reports submitted, the triggering incident is Y-G fault caused by flashover of Y-phase tension insulator of 220kV Bus-1 (near 220KV-TRIVA | 12 GI-1 KERALA 05-07-2026 17:00 05-07-2026 18:20 01:20 0 0 0.00% 0.00% 48525.17 44394.28 Tripping of 220kV Bus-1 & Bus-3 of 220kV Pothencode SS of KSEB As per the reports submitted, the triggering incident is Y-G fault caused by flashover of Y-phase tension insulator of 220kV Bus-1 (near 220KV-TRIVANDRUM- POTHENCODE-1 feeder). This resulted in the operation of busbar differential protection and tripped all elements connected to 220kV Bus-1 (including Bus-3 which is permanently coupled to Bus-1) of POTHENCODE SS of KSEB. 110kV was in service during the event. Therefore no load loss is observed. 220KV-POTHENCODE-TRIVANDRUM-3, 220KV-POTHENCODE- TRIVANDRUM-1, 220KV-EDAMON-POTHENCODE-2, 220KV- POTHENCODE-NEWKATAKADA-1, POTHENCODE - 220KV - Bus 1, POTHENCODE - 220KV - Bus 3 | grid_india_gd/grid_events/2026-07-01
G00363 | 2026-07 | 23 | GD-1 | Gujarat | GJ | Western | 2026-07-08T19:40 | 2026-07-09T00:20 | 4.67 | 190 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 6/3, resulting in a generation loss of 190 MW at Kotda madh S/S due to loss of evacuation path. | 4 GD-1 Gujarat 08-07-2026 19:40 09-07-2026 00:20 04:40 190 - 0.24% - 78385 64047 Complete outage of 220 kV Netra Kotda Madh S/S: At 19:40 hrs on 08-07-2026, the 220 kV Bhuj – Netra Kotda Madh transmission line tripped on B-phase to Earth fault due to throwing of a conducting object by an unknown person near tower no. 6/3, resulting in a generation loss of 190 MW at Kotda madh S/S due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj – Netra Kotda Madh | grid_india_gd/grid_events/2026-07-01
G00364 | 2026-07 | 24 | GD-1 | Gujarat | GJ | Western | 2026-07-09T14:00 | 2026-07-09T19:05 | 5.08 | 143 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 143 MW occurred at Gadhsisa S/S due to loss of evacuation path. | 5 GD-1 Gujarat 09-07-2026 14:00 09-07-2026 19:05 05:05 143 - 0.19% - 75857 58895 Complete outage of 220kV Gadhsisa S/S: At 14:00 Hrs on 09-07-2026, 220kV Bhuj–Gadhsisa line tripped on to B phase to ground fault due to foreign object is found at tower no. 36/1 B Phase. Generation loss of 143 MW occurred at Gadhsisa S/S due to loss of evacuation path. Due to only evacuating line GD occurred. Tripping of following Elements: 1. 220kV Bhuj–Gadhsisa | grid_india_gd/grid_events/2026-07-01
G00365 | 2026-07 | 58 | GI-2 | TAMILNADU , PONDICHERRY |  |  | 2026-07-10T13:02 | 2026-07-10T13:09 | 0.12 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GI-2 TAMILNADU , PONDICHERRY 10-07-2026 13:02 10-07-2026 13:09 00:07 0 0 0.00% 0.00% 53625.38 63851.92 Tripping of 400kV Bus-2 at NNTPP of NLC As per the reports submitted, SF6 interlock testing on the 400 kV GT-2 bay at NNTPP a false busbar trip was triggered due to a relay mapping error, which | 13 GI-2 TAMILNADU , PONDICHERRY 10-07-2026 13:02 10-07-2026 13:09 00:07 0 0 0.00% 0.00% 53625.38 63851.92 Tripping of 400kV Bus-2 at NNTPP of NLC As per the reports submitted, SF6 interlock testing on the 400 kV GT-2 bay at NNTPP a false busbar trip was triggered due to a relay mapping error, which cause opening of 400 kV Bus-2 and all connected elements (400KV/230KV NNTPP-ICT-2, Bus Coupler, 400KV-NNTPP-PUDUCHERRY-1, and 400KV-ARIYALUR-NNTPP-2 lines). After which the loading in ICT-1 increased and tripped due to overcurrent protection. This led to the Tripping of 400kV Bus-2 at NNTPP of NLC. 400KV-NNTPP-PUDUCHERRY-1, 400KV/230KV NNTPP-ICT-1, 400KV/230KV NNTPP-ICT-2, NNTPP - 400KV - Bus 2, 400KV- ARIYALUR-NNTPP-2 | grid_india_gd/grid_events/2026-07-01
G00366 | 2026-07 | 2 | GD-1 | Rajasthan | RJ | Northern | 2026-07-10T15:38 | 2026-07-10T18:13 | 2.58 | 0 | 105 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Rajasthan 10-07-2026 15:38 10-07-2026 18:13 02:35 0 105 0.00 0.14 71476 73392 i)220/132kV Duni(RS) has double main and transfer bus scheme at 220kV level. There are two 220kV lines connected at 220kV Duni s/s, viz 220 KV Duni(RS)-Jaipur South(PG) (RS) Ckt and 220 kV Duni(RS)–Kota(PG) (RS) Ckt | 2 GD-1 Rajasthan 10-07-2026 15:38 10-07-2026 18:13 02:35 0 105 0.00 0.14 71476 73392 i)220/132kV Duni(RS) has double main and transfer bus scheme at 220kV level. There are two 220kV lines connected at 220kV Duni s/s, viz 220 KV Duni(RS)-Jaipur South(PG) (RS) Ckt and 220 kV Duni(RS)–Kota(PG) (RS) Ckt. ii)During antecedent conditions, the 220 kV Duni(RS)–Kota(PG) (RS) Ckt had been under outage since 07.07.2026 due to a broken conductor between tower no. 19 and tower no. 20. Consequently, the 220 KV Duni(RS)-Jaipur South(PG) (RS) Ckt was the only 220 kV source feeding Duni (RS) substation and was carrying approximately 109 MW (as per SCADA data). iii)As reported, at 15:38 hrs, 220 KV Duni(RS)-Jaipur South(PG) (RS) Ckt tripped from Jaipur South(PG) end only due to R-Y phase to phase fault; fault was sensed in zone 3 from Jaipur South(PG) with fault current: Ir=~1.8 kA and Iy=~1.5kA from Jaipur South(PG) end. The exact fault location and the cause of the fault are yet to be shared. iv)Since the Jaipur South (PG) circuit was the only 220 kV source feeding Duni (RS) substation, its tripping resulted in a complete blackout of the 220/132 kV Duni (RS) substation. v)As per PMU at Jaipur South(PG), R-Y phase to phase fault was observed with delayed fault clearance time of 840 ms. vi)As per SCADA, change in demand of approx 105 MW was observed in Rajasthan control area. 1) 220 KV Duni(RS)-Jaipur South(PG) (RS) Ckt-1 | grid_india_gd/grid_events/2026-07-01
G00367 | 2026-07 | 25 | GD-1 | Gujarat | GJ | Western | 2026-07-10T18:33 | 2026-07-10T18:54 | 0.35 | 185 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 185 MW due to loss of evacuaton path. | 6 GD-1 Gujarat 10-07-2026 18:33 10-07-2026 18:54 00:21 185 - 0.23% - 82201 64713 Complete outage of 220 kV Nanikhakhar (GETCO): At 18:23 hrs/10-07-2026, at 220 kV Nanikhakhar (GETCO) Substation, the top L-clamp of the B-phase jumper of 220kV Nanikhakhar–Sindhodi Line-2, at the Bus-B (Bus- 2) isolator, broke. The jumper fell and got earthed through an electric arc on Bus-2, causing operation of Bus Bar Protection (87BB) Zone-2 and tripping of all bays connected to Bus-2 — Sindhodi Line-2, Suthri Line-2, Nakhtrana Line-1, Kukma Line, Adani (APL) Line-2, CGPL Line, 100 MVA TR-2, 100 MVA TR-4 and the Bus Coupler. Generation loss of 185 MW due to loss of evacuaton path. Tripping of following Elements: 1. Nanikhakhar–Sindhodi Line-2 | grid_india_gd/grid_events/2026-07-01
G00368 | 2026-07 | 26 | GD-1 | Gujarat | GJ | Western | 2026-07-11T13:17 | 2026-07-11T21:02 | 7.75 | 225 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss 225 MW occurred at 220 kV Sidhpur RE station due to loss of evacuation path. | 7 GD-1 Gujarat 11-07-2026 13:17 11-07-2026 21:02 07:45 225 - 0.31% - 72827 57862 Complete outage of 220kV Sidhpur S/S: At 13:17 hrs/ 11-07-26, 220kV Sidhpur Jamkhambaliya S/C tripped due to Rph-E fault. Generation loss 225 MW occurred at 220 kV Sidhpur RE station due to loss of evacuation path. Due to only evacuating line GD occurred. Tripping of following Elements: 1. 220kV Sidhpur Jamkhambaliya S/C | grid_india_gd/grid_events/2026-07-01
G00369 | 2026-07 | 3 | GI-2 | Haryana | HR | Northern | 2026-07-11T19:44 | 2026-07-11T21:59 | 2.25 | 0 | 252 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GI-2 Haryana 11-07-2026 19:44 11-07-2026 21:59 02:15 0 252 0.00 0.32 61182 79888 i)During the antecedent condition, Pole 2 and Pole 4 of the 800 kV HVDC Champa–Kurukshetra were under emergency shutdown. Pole 1 and Pole 3 were carrying a total of ~2680 MW power from Champa to Kurukshetra (~1340 MW | 3 GI-2 Haryana 11-07-2026 19:44 11-07-2026 21:59 02:15 0 252 0.00 0.32 61182 79888 i)During the antecedent condition, Pole 2 and Pole 4 of the 800 kV HVDC Champa–Kurukshetra were under emergency shutdown. Pole 1 and Pole 3 were carrying a total of ~2680 MW power from Champa to Kurukshetra (~1340 MW on each pole) (as per SCADA). ii)As reported, at 19:44 hrs, 800 kV HVDC Kurukshetra(PG) Pole 1 and Pole 3 were blocked from the Champa end due to the operation of Parallel Pole Protection, as both lanes of Pole 1 at Champa became unavailable due to failure of the S5008 measuring card. iii)As per the PMU at Kurukshetra(PG), no fault was observed in the system; however, voltage fluctuations were observed. iv)As per SCADA, no change in demand was observed in the Haryana control area. Approx 252MW change in Punjab demand was observed. As per SLDC Punjab change in demand was attributed to the operation of DF/DT Stage 1 at 17 number of 220kV feeders in Punjab Control Area v)Change in the power order of approximately 2680 MW occurred during the event. vi)As reported by CPCC1, S5008 measuring card is replaced. 1) 800 KV HVDC Kurukshetra(PG) Pole-1 2) 800 KV HVDC Kurukshetra(PG) Pole-3 | grid_india_gd/grid_events/2026-07-01
G00370 | 2026-07 | 27 | GD-1 | Gujarat | GJ | Western | 2026-07-12T02:23 | 2026-07-12T15:51 | 13.47 | 252 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 252 MW reported due to loss of evacuation path. | 8 GD-1 Gujarat 12-07-2026 02:23 12-07-2026 15:51 13:28 252 - 0.31% - 82215 66040 Complete outage of 220KV Khakharda S/S: At 02:23 Hrs/12-07-2026, 220KV Jamkhambaliya – Khakharda line tripped due to Y- phase to Earth fault. Generation loss of 252 MW reported due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220KV Jamkhambaliya – Khakharda Elements Tripped Details of Grid Events during the Month of July 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of July 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of | grid_india_gd/grid_events/2026-07-01
G00371 | 2026-07 | 4 | GI-2 | Haryana | HR | Northern | 2026-07-12T09:55 | 2026-07-12T16:10 | 6.25 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Haryana 12-07-2026 09:55 12-07-2026 16:10 06:15 0 0 0.00 0.00 62835 70007 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~1000 MW power from Champa to Kurukshetra (~250 MW on each Pole) (as per SCADA). ii)As reported, at 09:55 hrs, 800 KV HVDC Kurukshetra(PG) | 4 GI-2 Haryana 12-07-2026 09:55 12-07-2026 16:10 06:15 0 0 0.00 0.00 62835 70007 i)During antecedent condition, 800kV HVDC Champa-Kurukshetra was carrying total ~1000 MW power from Champa to Kurukshetra (~250 MW on each Pole) (as per SCADA). ii)As reported, at 09:55 hrs, 800 KV HVDC Kurukshetra(PG) Pole-1 & 2 blocked due to latching/activation of TOVC mode at Champa end due to mal operation of RPC (Reactive Power Control). iii)As per PMU at Kurukshetra (PG), no fault was observed in the system; however, fluctuation in voltage was observed after tripping. iv)As per SCADA, no change in demand in Haryana control area was observed. v)As per SCADA, there was no significant change in power order was observed; the power flow shifted to other two poles. vi)CPCC1 has reported that systems have been rebooted and now RPC is functioning as per desired logic. 1) 800 KV HVDC Kurukshetra(PG) Pole-1 2) 800 KV HVDC Kurukshetra(PG) Pole-2 | grid_india_gd/grid_events/2026-07-01
G00372 | 2026-07 | 5 | GD-1 | Rajasthan | RJ | Northern | 2026-07-13T17:44 | 2026-07-13T20:33 | 2.82 | 584 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | x)As per SCADA, solar Generation loss of approx 584 MW [66MW at RSVPL(IP), 92MW at RSRPL(IP), 88MW at AXPPL(IP), 1) 220 KV Fatehgarh_III(PG) - Bus 1,2,6,8 2) 400/220 kV 500 MVA ICT 1,3,4,5,8,9 and 10 at Fatehgarh_III(PG) 3) 220 KV RSVPL_SL_FTHG3_PG-Fatehgarh_III(PG) (RENEW SURYA VIHAAN PRIVATE LIMITED) Ckt-1 4) 220 KV Fatehgarh_III(PG)-RSRPL_Hyb_FTHG3_PG (RENEW SURYA ROSHNI PRIVATE LIMITED) Ckt-1 | 5 GD-1 Rajasthan 13-07-2026 17:44 13-07-2026 20:33 02:49 584 0 0.88 0.00 66171 82063 i)765/400/220kV Fatehgarh3 has six bus system at 220kV level with double main and transfer scheme. Main bus 1&2 are connected with main bus 5&6 through bus sectionalizer 224 and 223 respectively. Main bus 5&6 are connected with main bus 7&8 through bus sectionalizer 236 and 235 respectively.ii)220kV RSVPL(IP), 220kV RSRPL(IP), 220kV AXPPL(IP), 220kV ASEB1L(IP), 220kV RSAPL(IP), 220kV KREPL(IP), 220kV Energant(IP), 220kV XXPPL(IP), 220kV ABCRJ02(IP), and 220kV IBVOGT(IP) are connected to 765/400/220kV Fatehgarh3(PG) at 220kV level.iii)During antecedent condition, there were nine 400/220kV 500MVA ICTs were in service at Fatehgarh3(PG) and carrying ~80MW each. RSVPL(IP) was generating total 66 MW [Renew Saurya Pratap(IP) and Renew Saurya Vihan(IP) were generating approx 44 MW and 22 MW respectively], Renew Roshni (IP) was generating approx 92 MW, AXPPL(IP) was generating approx 88MW, ASEB1L(IP) was generating approx 59MW, RSAPL(IP) was generating approx 63MW, KREPL(IP) was generating approx 43MW, Energant(IP) was generating approx 11MW, XXPPL(IP) was generating approx 77MW, ABCRJ02(IP) was generating approx 41MW, and IBVOGT(IP) was generating approx 47 MW (as per SCADA).iv)As reported, at 17:44 hrs, busbar Protection of 220kV Bus2 at Fatehgarh3(PG) operated due to the failure of the R-phase CT of bus sectionalizer bay 223. Subsequently, the bus coupler connecting Bus 1 and Bus 2 failed to open, | grid_india_gd/grid_events/2026-07-01
G00373 | 2026-07 | 6 | GD-1 | Rajasthan | RJ | Northern | 2026-07-14T15:36 | 2026-07-15T09:55 | 18.32 | 223 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | v)As per SCADA, generation loss of approx 223 MW at Gorbea(IP) was observed. | 6 GD-1 Rajasthan 14-07-2026 15:36 15-07-2026 09:55 18:19 223 0 0.28 0.00 79781 90617 i)Generation of 220kV Gorbea(IP) station evacuates through 220 KV Bhadla_2 (PG)-GSPL_SL_BHD2_PG (Gorbea_SPL) Ckt. ii)During antecedent condition, 220kV Gorbea(IP) station was generating approx 223 MW (as per SCADA). iii)As reported, at 15:36hrs, 220 KV Bhadla_2 (PG)-GSPL_SL_BHD2_PG (Gorbea_SPL) Ckt tripped due to operation of differential protection due to Y-B phase to phase fault with fault current Iy=14.4kA and Ib=14.6kA at Bhadla2(PG) end, which led to complete blackout out of 220kV Gorbea(IP) S/s. iv)As per PMU at Bhadla2(PG), Y-B phase to phase fault was observed with fault clearing time of 80ms. v)As per SCADA, generation loss of approx 223 MW at Gorbea(IP) was observed. 1) 220 KV Bhadla_2 (PG)-GSPL_SL_BHD2_PG (Gorbea_SPL) Ckt-1 | grid_india_gd/grid_events/2026-07-01
G00374 | 2026-07 | 7 | GD-1 | Chandigarh | CH | Northern | 2026-07-14T16:37 | 2026-07-14T17:42 | 1.08 | 0 | 195 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GD-1 Chandigarh 14-07-2026 16:37 14-07-2026 17:42 01:05 0 195 0.00 0.22 74377 86841 i)220/66kV Kishangarh Mani(CHD) is connected with 400/220kV Nalagarh(PG) s/s through 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-1 and Ckt-2. ii)During antecedent conditions, 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-1 and Ckt-2 were carrying approximately 91 MW each (as per SCADA data). iii)As reported, at 16:37 hrs, 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-1 tripped from Nalagarh(PG) end only due to R-Y phase to phase fault; fault was sensed in zone 1 from Nalagarh(PG) with fault distance of 1.9km and fault current: Ir=~19.8 kA and Iy=~19.3kA from Nalagarh(PG) end. iv)Since the 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-1 failed to open from Kishangarh Mani(CHD) end, 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-2 sensed same fault in zone 2 with fault distance 79.69km, and fault current: Ir=0.71 kA and Iy=2.29kA from Nalagarh(PG) end, resulted in tripping of second circuit as well. v)As per PMU at Nalagarh(PG), R-Y phase to phase fault was observed with fault clearance time of 120 ms. vi)As per SCADA, change in demand of approx 195 MW was observed in Chandigarh control area. 1) 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-1 2) 220 KV Nalagarh(PG)-Kishan(CHD) (CHD) Ckt-2 Details of Grid Events during the Month of July 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load | grid_india_gd/grid_events/2026-07-01
G00375 | 2026-07 | 28 | GD-1 | Gujarat | GJ | Western | 2026-07-14T21:30 | 2026-07-15T09:45 | 12.25 | 150 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 150 MW Occurred at Vadva (GIWEL-II) Wind Power Plant due to loss of evacuation path. | 9 GD-1 Gujarat 14-07-2026 21:30 15-07-2026 09:45 12:15 150 - 0.17% - 88907 69612 Complete outage of 220kV Vadva S/S: At 21:30 hrs / 14-07-2026, 220 kV Bhuj-Vadva-1 tripped on R-E Fault, auto recloser was unsuccessful at Bhuj end and auto recloser was not attempted at Vadva end. A test charging attempt was made at 02:31 hrs / 15-07-2026, but the line did not hold. During subsequent patrolling, insulator failure was found. Generation loss of 150 MW Occurred at Vadva (GIWEL-II) Wind Power Plant due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj-Vadva-1 | grid_india_gd/grid_events/2026-07-01
G00376 | 2026-07 | 29 | GD-1 | Gujarat | GJ | Western | 2026-07-14T23:07 | 2026-07-15T00:35 | 1.47 | 96 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 96 MW occurred at Ostro Wind Power plant due to loss of evacuation path. | 10 GD-1 Gujarat 14-07-2026 23:07 15-07-2026 00:35 01:28 96 - 0.11% - 89263 69814 Complete outage of 220kV Ostro S/S: At 23:07 Hrs /14-07-2026, 220 kV Bachau-Ostro Line-1 & Line-2 tripped due to Y-N fault without A/R attempt and DT received at Bachau end. Generation loss of 96 MW occurred at Ostro Wind Power plant due to loss of evacuation path. Due to tripping of both evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bachau-Ostro Line-1 2. 220 kV Bachau-Ostro Line-2 | grid_india_gd/grid_events/2026-07-01
G00377 | 2026-07 | 35 | GD-1 | Gujarat | GJ | Western | 2026-07-15T00:35 | 2026-07-15T00:35 | 0 | 91 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 91 MW occurred at Gadhsisa S/S due to the loss of evacuation path. | 16 GD-1 Gujarat 15-07-2026 00:35 15-07-2026 00:35 00:00 91 - 0.12% - 78264 63963 Complete outage of 220kV Gadhsisa S/S: At 23:39 Hrs/ 20-07-2026, 220kV Bhuj- Gadhsisa line tripped on R-phase-E fault. Generation loss of 91 MW occurred at Gadhsisa S/S due to the loss of evacuation path. Due to tripping of only available evacuating line GD occurred. Tripping of following Elements: 1. 220kV Bhuj–Gadhsisa | grid_india_gd/grid_events/2026-07-01
G00378 | 2026-07 | 30 | GD-1 | Gujarat | GJ | Western | 2026-07-15T05:39 | 2026-07-15T13:40 | 8.02 | 140 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 140 MW occurred at Khakharda S/S due to loss of evacuation path. | 11 GD-1 Gujarat 15-07-2026 05:39 15-07-2026 13:40 08:01 140 - 0.17% - 81590 67168 Complete outage of 220kV Khakharda S/S: At 05:39 Hrs/15-07-2026, 220KV Jamkhambaliya – Khakharda line tripped due to B- phase to Earth fault. Generation loss of 140 MW occurred at Khakharda S/S due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1.220KV Jamkhambaliya – Khakharda | grid_india_gd/grid_events/2026-07-01
G00379 | 2026-07 | 8 | GI-2 | Rajasthan | RJ | Northern | 2026-07-16T04:44 | 2026-07-16T07:40 | 2.93 | 620 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, Generation loss of approx 620 MW was observed at Rajwest(RW). | 8 GI-2 Rajasthan 16-07-2026 04:44 16-07-2026 07:40 02:56 620 0 1.00 0.00 62017 79374 i)400/220kV Rajwest(RW) has one and half breaker scheme at 400kV level and double main bus and transfer bus scheme at 220kV level. ii)During antecedent condition, 135 MW Rajwest (IPP) LTPS - UNIT 2, 4, 5, 6, 7 & 8 were in running condition and were generating approx 101 MW, 93 MW, 134 MW, 134 MW, 125 MW and 134 MW respectively (as per SCADA). 400 KV Jodhpur(RS)-Rajwest(RW) (RS) Ckt and 400 KV Rajwest(RW)-GSS Pachpadra (RS) Ckt were already under outage since 01.06.2026. iii)As reported, at 04:44 hrs, 400 KV Rajwest(RW)-Barmer (RS) Ckt tripped as DT received at Rajwest end from Barmer end, DR/EL and fault details are yet to be shared from Barmer(RS) end. iv)During the same time, 400/220 KV 315 MVA ICT Rajwest(RS) also tripped due to overloading. As per DR, over-current protection operated in ICT. v)This resulted in the loss of the remaining 400 kV evacuation path from Rajwest and 135 MW Rajwest (IPP) LTPS - UNIT 4, 5, 6, 7 & 8 tripped on over-frequency due to loss of evacuation path. vi)As per PMU at Bhinmal(PG), no fault was observed during the event. vii)As per SCADA, Generation loss of approx 620 MW was observed at Rajwest(RW). 1) 400 kV Barmer(RS)-Rajwest(RW) (RS) Ckt-1 2) 400/220 kV 315 MVA ICT 1 at Rajwest(RW) 3) 135 MW Rajwest (IPP) LTPS - UNIT 4 4) 135 MW Rajwest (IPP) LTPS - UNIT 5 5) 135 MW Rajwest (IPP) LTPS - UNIT 6 6) 135 MW Rajwest (IPP) LTPS - UNIT 7 7) 135 MW Rajwest (IPP) LTPS | grid_india_gd/grid_events/2026-07-01
G00380 | 2026-07 | 59 | GI-1 | Andhra Pradesh | AP | Southern | 2026-07-16T11:52 | 2026-07-16T12:06 | 0.23 | 0 | 1150 | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GI-1 ANDHRA PRADESH 16-07-2026 11:52 16-07-2026 12:06 00:14 0 1150 0.00% 1.60% 63065.99 71995.41 Tripping of 220kV Bus-1 and 2 at Vemagiri(AP) of APTRANSCO As per the submitted reports, the triggering incident was R-G fault in 220kV Vemagiri Bus coupler. Immediately, 220kV Bus-1 & Bus-2 BBP opera | 14 GI-1 ANDHRA PRADESH 16-07-2026 11:52 16-07-2026 12:06 00:14 0 1150 0.00% 1.60% 63065.99 71995.41 Tripping of 220kV Bus-1 and 2 at Vemagiri(AP) of APTRANSCO As per the submitted reports, the triggering incident was R-G fault in 220kV Vemagiri Bus coupler. Immediately, 220kV Bus-1 & Bus-2 BBP operated tripping all elements connected to the bus including Vemagiri ICTs. This led to tripping of 220kV Bus-1 & Bus-2 of 220kV Vemagiri_AP. Tripping of the ICTs led to over loading of 400kV/220kV Guddigudem ICT-1 & 2 and the ICTs tripped on overloading. 400KV/220KV VEMAGIRI_AP-ICT-1, 400KV/220KV VEMAGIRI_AP-ICT-2, 400KV/220KV VEMAGIRI_AP-ICT-3, 400KV/220KV VEMAGIRI_AP-ICT-4, 400KV/220KV GUDDIGUDEM-ICT-1, 400KV/220KV GUDDIGUDEM-ICT-2 | grid_india_gd/grid_events/2026-07-01
G00381 | 2026-07 | 31 | GD-1 | Gujarat | GJ | Western | 2026-07-16T16:13 | 2026-07-16T17:15 | 1.03 | 237 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GD-1 Gujarat 16-07-2026 16:13 16-07-2026 17:15 01:02 237 - 0.27% - 89028 73086 Complete outage of 220kV Ostro S/S: At 16:13 hrs / 16-07-2026, 220 kV Bhachau-Ostro-1 tripped on B-E Fault, auto recloser unsuccessful at Bhachau end and auto recloser was not attempted at Ostro end (3 phase tripped for fault in single phase) Generation loss of 237 MW Occurred at Ostro (Renew Power) due to loss of ev | 12 GD-1 Gujarat 16-07-2026 16:13 16-07-2026 17:15 01:02 237 - 0.27% - 89028 73086 Complete outage of 220kV Ostro S/S: At 16:13 hrs / 16-07-2026, 220 kV Bhachau-Ostro-1 tripped on B-E Fault, auto recloser unsuccessful at Bhachau end and auto recloser was not attempted at Ostro end (3 phase tripped for fault in single phase) Generation loss of 237 MW Occurred at Ostro (Renew Power) due to loss of evacuation path. Due to tripping of only available evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bachau-Ostro Line-1 2. 220 kV Bachau-Ostro Line-2 | grid_india_gd/grid_events/2026-07-01
G00382 | 2026-07 | 9 | GD-1 | UP & Uttarakhand |  |  | 2026-07-17T05:00 | 2026-07-17T05:52 | 0.87 | 680 | 131 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, change in demand of approx 131 MW was observed in UƩarakhand control area; and Generation loss of ~354 MW at Alaknanda HEP, ~220MW at Vishnuprayag HEP, and ~106MW at Singoli Bhatwari HEP. | 9 GD-1 UP & Uttarakhand 17-07-2026 05:00 17-07-2026 05:52 00:52 680 131 1.08 0.16 62802 80848 i)400kV Alaknanda(UP) has one and half breaker scheme at 400kV level. 400kV Vishnuprayag(UP) has double main bus scheme. 400/220/132kV Srinagar(UK) has double main and transfer scheme at both 400kV and 220kV level. 220kV Singoli Bhatwari(IP) has double main bus scheme.ii)During antecedent condition, all four units at Alaknanda HEP were in running condition and were generating ~354MW, all four units at Vishnuprayag HEP were in running condition and were generating ~442MW, and all three units at Singoli Bhatwari were in running condition and were generating ~106MW. iii)As reported, at 05:00 hrs, B-N phase to ground fault occurred at 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt; fault was sensed in zone 1 from both ends with fault current of 6.3kA from Muzaffarnagar end and 21.75kA from Alaknanda end; fault distance was 46.4km from Muzaffarnagar. As per PMU, fault clearing time was 80ms. Based on the DR shared by both the ends, it was observed after ~1000ms of clearing the B-phase fault, the remaining two phases tripped and no auto recloser aƩempt was made. iv)As reported, after the tripping of the 400 KV Alaknanda GVK(UPC)-Muzaffarnagar (UP) Ckt, the loading on the 400 kV bus coupler at Vishnuprayag increased, resulting in the operation of overcurrent protection. The subsequent tripping of the bus coupler led to the separation of both 400 kV buses at Vishnuprayag, thereby isolating | grid_india_gd/grid_events/2026-07-01
G00383 | 2026-07 | 10 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-07-17T11:08 | 2026-07-17T12:35 | 1.45 | 0 | 326 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GD-1 Jammu & Kashmir 17-07-2026 11:08 17-07-2026 12:35 01:27 0 326 0.00 0.37 82713 89297 i)220/132kV Barn(JK) is connected with 400/220kV Kishanpur(PG) through 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)SPS has been installed at 400/220kV Kishanpur(PG) s/s to facilitate shutdown o | 10 GD-1 Jammu & Kashmir 17-07-2026 11:08 17-07-2026 12:35 01:27 0 326 0.00 0.37 82713 89297 i)220/132kV Barn(JK) is connected with 400/220kV Kishanpur(PG) through 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)SPS has been installed at 400/220kV Kishanpur(PG) s/s to facilitate shutdown of Salal generation for silt flushing. As per SPS logic, if loading of any 315MVA ICT at Kishanpur(PG) exceeds 105% of the rated capacity, 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) D/C shall trip. iii)During antecedent condition, Loading of 315MVA ICT 1&2 was ~280MW and ~172MVAR and was in increasing trend, and 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 were carrying ~165 MW each (as per SCADA). iv)As reported, at 11:08 hrs, 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 tripped due to operation of SPS at Kishanpur(PG). v)As 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) D/C was the only 220kV source for 220/132kV Barn(JK) s/s, tripping of these circuits resulted in complete blackout of 220/132kV Barn(JK) s/s. vi)As per SCADA, change in demand of approx 326MW is observed in J&K control area. 1) 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-1 2) 220 KV Kishanpur(PG)-Barn(JK) (PDD JK) Ckt-2 | grid_india_gd/grid_events/2026-07-01
G00384 | 2026-07 | 32 | GD-1 | Gujarat | GJ | Western | 2026-07-17T22:13 | 2026-07-18T09:52 | 11.65 | 70 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 70 MW occurred at 220kV Naranpar S/S due to loss of evacuation path and station went dark. | 13 GD-1 Gujarat 17-07-2026 22:13 18-07-2026 09:52 11:39 70 - 0.08% - 86417 67917 Complete outage of 220kV Naranpar S/S: At 22:13 Hrs /17-07-2026, 220 kV Bhuj- Naranpar S/C line tripped on Y-E fault. Generation loss of 70 MW occurred at 220kV Naranpar S/S due to loss of evacuation path and station went dark. Due to tripping of both evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj- Naranpar S/C | grid_india_gd/grid_events/2026-07-01
G00385 | 2026-07 | 33 | GD-1 | Madhya Pradesh | MP | Western | 2026-07-18T12:34 | 2026-07-18T18:17 | 5.72 | 48 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 14 GD-1 Madhya Pradesh 18-07-2026 12:34 18-07-2026 18:17 05:43 48 - 0.06% - 84169 71473 Complete outage of 220kV Hajratpur S/S: At 12:34 Hrs/18-07-2026, 220 kV Hajratpur-Rajgarh-1 line breaker and bus-coupler breaker tripped due to loss of DC supply to the circuit breakers, resulting in generation loss of 48 MW at 220 kV Hajratpur (Sprng Energy) due to loss of evacuation path. | 14 GD-1 Madhya Pradesh 18-07-2026 12:34 18-07-2026 18:17 05:43 48 - 0.06% - 84169 71473 Complete outage of 220kV Hajratpur S/S: At 12:34 Hrs/18-07-2026, 220 kV Hajratpur-Rajgarh-1 line breaker and bus-coupler breaker tripped due to loss of DC supply to the circuit breakers, resulting in generation loss of 48 MW at 220 kV Hajratpur (Sprng Energy) due to loss of evacuation path. Tripping of following Elements: 1. 220 kV Hajratpur-Rajgarh-1 | grid_india_gd/grid_events/2026-07-01
G00386 | 2026-07 | 11 | GD-1 | Rajasthan | RJ | Northern | 2026-07-19T15:34 | 2026-07-19T18:03 | 2.48 | 141 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx ~290MW at SRI8PL & ~124MW at SRI9PL (IP) were observed. | 11 GD-1 Rajasthan 19-07-2026 15:34 19-07-2026 18:03 02:29 141 0 0.19 0.00 75803 84642 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) was generating approx 414 MW (as per SCADA). iii)As reported, at 15:34 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped. As per DR, no fault was observed; however, zone 3 protection operated and line tripped after of ~800ms. This led to complete blackout of 400kV Serentica 8 & 9 (IP) S/s. iv)At the same time, 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt also tripped. Exact reason and nature of protection operated is yet to be shared. v)As per PMU at Fatehgarh3(IP), no fault was observed. vi)As per SCADA, generation loss of approx ~290MW at SRI8PL & ~124MW at SRI9PL (IP) were observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt 2) 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt-1 | grid_india_gd/grid_events/2026-07-01
G00387 | 2026-07 | 12 | GI-1 | Uttarakhand | UK | Northern | 2026-07-20T12:29 | 2026-07-20T13:23 | 0.9 | 0 | 183 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-1 Uttarakhand 20-07-2026 12:29 20-07-2026 13:23 00:54 0 183 0.00 0.22 73294 81459 i)220kV Roorkee(UK) S/s has double main and transfer bus scheme at 220kV level. ii)As reported, under antecedent system conditions, the bus coupler at 220kV level was open. The 220 kV Roorkee(PG)–Roorkee(UK)(PTCU | 12 GI-1 Uttarakhand 20-07-2026 12:29 20-07-2026 13:23 00:54 0 183 0.00 0.22 73294 81459 i)220kV Roorkee(UK) S/s has double main and transfer bus scheme at 220kV level. ii)As reported, under antecedent system conditions, the bus coupler at 220kV level was open. The 220 kV Roorkee(PG)–Roorkee(UK)(PTCUL) circuit, the 220 kV Roorkee(UK)–Railway(UK) circuit, and the 160 MVA, 220/132 kV ICT-1 and ICT-2 were connected to Bus-1. The 220 kV Nara(UP)–Roorkee(UK) circuit and the 50 MVA, 220/33 kV ICT-1 and ICT-2 were connected to Bus-2. The 220 kV Roorkee(PG)–Roorkee(UK)(PTCUL) circuit was carrying 192 MW from Roorkee (PG) to Roorkee (UK), as per SCADA data. iii)As reported, at 12:29 hrs, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 tripped on Y-N Phase to earth fault with fault distance of 5.9km from Roorkee(PG) end and 10.42KM from Roorkee(UK) end. As per DR, fault was sensed in zone 1 from Roorkee(PG) end with fault current of ~13.4kA, fault clearing time was ~80ms; fault was sensed in zone 2 from Roorkee(UK) end with fault current of ~3.1kA, fault clearing time was ~440ms. iv)As per the DR, the carrier was not sent from the Roorkee(PG) end; hence, the fault was cleared from Roorkee(UK) with a delay of ~440ms. v)Tripping of the 220 kV Roorkee(PG)–Roorkee(UK)(PTCUL) ckt resulted in the outage of Bus-1 and the other elements connected to the bus, leading to load loss. vi)As per PMU at Roorkee(PG), Y-N Phase to earth fault was observed with fault clearance time of ~80 msec from Roorkee( | grid_india_gd/grid_events/2026-07-01
G00388 | 2026-07 | 34 | GD-1 | Gujarat | GJ | Western | 2026-07-20T23:39 | 2026-07-21T14:32 | 14.88 | 229 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 144 MW and 85 MW occurred at Baranda (Avikiran) Wind power plant due to loss of evacuation path and Devsar (Ayaana Power) Wind power plant due to tripping of 220 kV Devsar-ICT-1. | 15 GD-1 Gujarat 20-07-2026 23:39 21-07-2026 14:32 14:53 229 - 0.27% - 83729 69642 Complete outage of 220kV Devsar S/S: At 15:43 hrs / 20-07-2026, 220 kV Bhuj-Devsar-1 S/C auto reclosed successfully on R-E fault. Simultaneously, 220 kV Devsar-ICT-1 and 220 kV Baranda-ICT-2 tripped which is undesirable. 220 kV Bhuj-Baranda-1 S/C tripped due to LBB protection operation of 220 kV Baranda-ICT-2 bay at 220 kV End. Generation loss of 144 MW and 85 MW occurred at Baranda (Avikiran) Wind power plant due to loss of evacuation path and Devsar (Ayaana Power) Wind power plant due to tripping of 220 kV Devsar-ICT-1. Due to loss of only evacuation path of respective station GD occurred. Tripping of following Elements: 1. 220 kV Bhuj-Devsar-1 S/C | grid_india_gd/grid_events/2026-07-01
G00389 | 2026-07 | 36 | GD-1 | Gujarat | GJ | Western | 2026-07-21T00:20 | 2026-07-21T06:01 | 5.68 | 300 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 300 MW occurred at Nakhatrana & Dedhiya. | 17 GD-1 Gujarat 21-07-2026 00:20 21-07-2026 06:01 05:41 300 - 0.40% - 74573 63100 Complete outage of 220kV Nakhatrana S/S: At 00:20 hrs/21-07-2026, 220 kV Bhuj II-Nakhatrana (Adani) line tripped on R-Phase to earth fault. The radial 220 kV Nakhatrana-Dedhiya line also de-energised consequent to loss of source. Generation loss of 300 MW occurred at Nakhatrana & Dedhiya. Due to tripping of only available evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj II-Nakhatrana | grid_india_gd/grid_events/2026-07-01
G00390 | 2026-07 | 37 | GD-1 | Gujarat | GJ | Western | 2026-07-21T03:01 | 2026-07-21T08:45 | 5.73 | 65 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 65 MW Occurred at Nanavalka (Alfanar) due to loss of evacuation path. | 18 GD-1 Gujarat 21-07-2026 03:01 21-07-2026 08:45 05:44 65 - 0.09% - 70972 59715 Complete outage of 220kV Nanavalka S/S: At 03:01 hrs / 21-07-2026, 220 kV Nanavalka-ICT-2 tripped on differential protection operation due to failure of Y phase Post Insulator 220 kV Nanavalka-ICT-2 Bus-1 side Isolator. 220 kV Nanavalka-Bus Coupler Bay (203 Bay) was in service and it failed to operate due to low SF-6 pressure resulting in transient overcurrent protection operation and tripping 220 kV Bhuj-Nanavalka-1 S/C. Generation loss of 65 MW Occurred at Nanavalka (Alfanar) due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Nanavalka-Bhuj-1 | grid_india_gd/grid_events/2026-07-01
G00391 | 2026-07 | 13 | GD-1 | Rajasthan | RJ | Northern | 2026-07-21T09:55 | 2026-07-21T11:35 | 1.67 | 420 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 420MW at SRI8PL(IP) & SRI9PL(IP) was observed. | 13 GD-1 Rajasthan 21-07-2026 09:55 21-07-2026 11:35 01:40 420 0 0.59 0.00 71654 73622 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) was generating approx 420 MW (as per SCADA). iii)As reported, at 09:55 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped. As per DR, no fault was observed; however, zone 3 protection operated, and line tripped after delay of ~800ms. This led to complete blackout of 400kV Serentica 8 & 9 (IP) S/s. iv)At the same time, 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt also tripped. Exact reason and nature of protection operated is yet to be shared. v)As per PMU at Fatehgarh3(IP), no fault was observed. vi)As per SCADA, generation loss of approx 420MW at SRI8PL(IP) & SRI9PL(IP) was observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt 2) 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of July 2026 in Northern Region Elements Tripped Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / | grid_india_gd/grid_events/2026-07-01
G00392 | 2026-07 | 38 | GD-1 | Gujarat | GJ | Western | 2026-07-22T01:45 | 2026-07-22T09:25 | 7.67 | 172 |  | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 172 MW occurred at Nakhatrana (Wind) S/S due to loss of evacuation path. | 19 GD-1 Gujarat 22-07-2026 01:45 22-07-2026 09:25 07:40 172 - 0.25% - 69688 58145 Complete outage of 220kV Nakhatrana S/S: At 01:45 hrs/22.07.2026, 220 kV Bhuj-II–Nakatrana-1 line tripped from the Nakhatrana end due to an R-E fault. Generation loss of 172 MW occurred at Nakhatrana (Wind) S/S due to loss of evacuation path. As 220 kV Nakhatrana–Dhedhiya being radial line the power flow on line become zero. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj II-Nakhatrana | grid_india_gd/grid_events/2026-07-01
G00393 | 2026-07 | 39 | GD-1 | Gujarat | GJ | Western | 2026-07-22T03:23 | 2026-07-22T05:08 | 1.75 | 710 |  | FALSE | FALSE | FALSE | FALSE | FALSE | As reported by MP SLDC, 640 MW generation loss occurred. | 20 GD-1 Gujarat 22-07-2026 03:23 22-07-2026 05:08 01:45 710 - 1.18% - 60198 59374 Complete outage of 220kV Sanjay Gandhi S/S: At 03:23 Hrs/22-07-2026, While synchronizing 220 kV Sanjay Gandhi Unit 2, all the elements connected to 220 kV Birsinghpur (Sanjay Gandhi) Bus 2 tripped on LBB protection operation. At the same time, Sanjay Gandhi Unit 5 (500 MW) connected to 400 kV side also tripped. 220 kV Birsinghpur Interconnector 2&4, 220 kV Birsinghpur- Panagar, 220 kV Birsinghpur- Shahdol, 220 kV Birsinghpur- Manpur, 220 kV Birsinghpur Bus coupler, Sanjay Gandhi Unit 3 (210 MW) and Sanjay Gandhi Unit 5 (500 MW) tripped during the event. As reported by MP SLDC, 640 MW generation loss occurred. Tripping of following Elements: 1. Sanjay Gandhi Unit 3 (210 MW) 2. Sanjay Gandhi Unit 5 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of July 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) | grid_india_gd/grid_events/2026-07-01
G00394 | 2026-07 | 40 | GD-1 | Gujarat | GJ | Western | 2026-07-22T05:54 | 2026-07-22T09:32 | 3.63 | 10 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 9.7 MW Occurred at Morjar (Srijan) due to loss of evacuation path. | 21 GD-1 Gujarat 22-07-2026 05:54 22-07-2026 09:32 03:38 10 - 0.01% - 68980 58267 Complete outage of 220kV Srinan Morjar S/S: At 05:24 hrs / 22-07-2026, 220 kV Bhuj II-Morjar-1 tripped on Y-E Fault. Generation loss of 9.7 MW Occurred at Morjar (Srijan) due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj II-Morjar-1 | grid_india_gd/grid_events/2026-07-01
G00395 | 2026-07 | 41 | GD-1 | Gujarat | GJ | Western | 2026-07-22T06:15 | 2026-07-22T15:31 | 9.27 | 40 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 40 MW occurred at Kotda Madh S/S due to loss of evacuation path. | 22 GD-1 Gujarat 22-07-2026 06:15 22-07-2026 15:31 09:16 40 - 0.06% - 69148 60184 Complete outage of 220kV Kotda Madh S/S: At 06:15Hrs/ 22-07-2026, 220KV Kotda Madh Bhuj-1 line tripped due to R- phase to Earth fault. Generation loss of 40 MW occurred at Kotda Madh S/S due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220KV Kotda Madh Bhuj-1 | grid_india_gd/grid_events/2026-07-01
G00396 | 2026-07 | 14 | GI-2 | Uttar Pradesh | UP | Northern | 2026-07-22T22:19 | 2026-07-23T03:03 | 4.73 | 972 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, generation loss of ~972 MW was observed at Jawaharpur_TPS. | 14 GI-2 Uttar Pradesh 22-07-2026 22:19 23-07-2026 03:03 04:44 972 0 1.61 0.00 60198 82221 i)765/400/220kV Jawaharpur(UP) has one and half breaker scheme in 765kV & 400kV and double main bus scheme in 200kV. It comprises 2 X 660MW of generation. ii)During antecedent condition, 660MW Jawaharpur TPS - Unit1 and Unit2 were generating ~476 MW and ~485MW respectively. 765 KV Gr .Noida_2(UPC)-Jawaharpur_TPS (UP) line was carrying ~895 MW, 765 KV Jawaharpur_TPS-Mainpuri (UP) line was carrying ~492MW and loading of 765/400kV 1500MVA ICT1 & ICT2 were ~277MW and ~280MW respectively. iii)As reported, at 22:19 hrs on 22.07.2026, 765 KV Gr .Noida_2(UPC)-Jawaharpur_TPS (UP) Ckt tripped on Y-N fault due to Y phase insulator broken at tower 1.4 km from Jawaharpur end. Fault was sensed in zone 1 from Jawaharpur and zone 2 from Gr.Noida with fault current of 18kA and 5.16kA from Jawaharpur and Gr.Noida respectively. iv)As per DR received, unsuccessful A/R aƩempt was observed. However, delayed opening of breaker (~360 msec) was observed during A/R aƩempt. v)At same time, all four ICTs i.e., 2*1500 MVA 765/400kV & 2*500 MVA 400/220kV and GT-I & II at Jawaharpur TPS tripped on overcurrent earth fault protection operation. As per DR, all the ICTs and GTs tripped on overcurrent earth fault protection operation (stage-2, DT) during 2nd fault instant when there was delayed opening of line CB during A/R. Approx 3.3kA fault current was recorded at 400kV side of 765/400kV ICT. vi)Upon reviewing the prote | grid_india_gd/grid_events/2026-07-01
G00397 | 2026-07 | 44 | GD-1 | Gujarat | GJ | Western | 2026-07-23T06:57 | 2026-07-23T08:42 | 1.75 | 384 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 25 GD-1 Gujarat 23-07-2026 06:57 23-07-2026 08:42 01:45 384 - 0.59% - 64880 62275 Complete outage of 220kV New Kharadpada S/S: At 06:57 Hrs/23-07-2026, 220 kV Kala- New Kharadpada 1&2 tripped on Y-B phase fault & R-E fault respectively. Prior to the event, All 400, 220 kV lines & ICTs at Vapi (PG) h | 25 GD-1 Gujarat 23-07-2026 06:57 23-07-2026 08:42 01:45 384 - 0.59% - 64880 62275 Complete outage of 220kV New Kharadpada S/S: At 06:57 Hrs/23-07-2026, 220 kV Kala- New Kharadpada 1&2 tripped on Y-B phase fault & R-E fault respectively. Prior to the event, All 400, 220 kV lines & ICTs at Vapi (PG) hand tripped due to station flooding. Due to non-availability of Source from Vapi (PG), 220 kV New Kharadpada, Kharadpada & Bhilosa fed from 400/220 kV Kala s/s. With the tripping of 220 kV Kala- New Kharadpada 1&2, 220 kV New Kharadpada, Kharadpada & Bhilosa went dark. As per SCADA, load loss of 384 MW occurred due to the event. Tripping of following Elements: 1. 220 kV Kala- New Kharadpada 1 2. 220 kV Kala- New Kharadpada 2 | grid_india_gd/grid_events/2026-07-01
G00398 | 2026-07 | 42 | GD-1 | Gujarat | GJ | Western | 2026-07-23T23:57 | 2026-07-24T01:45 | 1.8 | 800 |  | FALSE | FALSE | FALSE | FALSE | TRUE | Due to loss of evacuation path generation loss of approx 800 MW was observed. | 23 GD-1 Gujarat 23-07-2026 23:57 24-07-2026 01:45 01:48 800 - 1.11% - 71873 54933 Complete outage of 220kV Bhuj PS S/S: At 23:57 Hrs/23-07-2026, 220 kV Bhuj PS Section C of Bus 1 and 2 got tripped. Due to which 220 kV Bhuj PS-Alfanar S/c, 220 kV Bhuj PS-Netra S/c, 220 kV Bhuj PS- Gadhsisa S/c, 220 kV Bhuj PS-Baranda S/c connected to the section got tripped. Due to protection issues 220 kV Bhuj PS- Vadva S/c and 220 kV Bhuj PS- Ratadiya D/c lines connected to other sections were also tripped from RE plant ends. After Inspection fault was observed in Bay 232 HGIS. Due to loss of evacuation path generation loss of approx 800 MW was observed. Tripping of following Elements: 1. 220 kV Bhuj PS- Vadva S/c | grid_india_gd/grid_events/2026-07-01
G00399 | 2026-07 | 45 | GD-1 | Gujarat | GJ | Western | 2026-07-24T01:14 | 2026-07-24T05:18 | 4.07 | 0 |  | TRUE | FALSE | FALSE | FALSE | TRUE | No generation loss was reported, as the incident occurred during non- solar hours. | 26 GD-1 Gujarat 24-07-2026 01:14 24-07-2026 05:18 04:04 0 - 0.00% - 67218 53470 Complete outage of 220kV GSEC(S) S/S: At 01:14 Hrs on 24.07.2026, all 400 kV elements at GSEC(S) tripped following the operation of the busbar protection due to a flashover at the 400 kV side of 400/33 kV ICT-4. As a result, the 400 kV GSEC(S)–KPS-2 line also tripped, leading to loss of supply at GSEC(S). No generation loss was reported, as the incident occurred during non- solar hours. Tripping of following Elements: 1. 400 kV GSEC(S)–KPS-2 | grid_india_gd/grid_events/2026-07-01
G00400 | 2026-07 | 43 | GD-1 | Gujarat | GJ | Western | 2026-07-24T05:41 | 2026-07-24T11:28 | 5.78 | 177 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of only evacuating line caused generation loss of around 177 MW. | 24 GD-1 Gujarat 24-07-2026 05:41 24-07-2026 11:28 05:47 177 - 0.26% - 67788 55186 Complete outage of 220kV Sitac S/S: At 05:41 hrs/24.07.2026, the 220 kV Sitac – Bhuj-II Circuit-1 tripped due to R-phase to earth fault. Due to tripping of only evacuating line caused generation loss of around 177 MW. After inspection, test charging attempt was taken at 09:11hrs, but immediately hand tripped from Bhuj-II end due to sparking observed in line isolator. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Sitac – Bhuj-II Circuit- | grid_india_gd/grid_events/2026-07-01
G00401 | 2026-07 | 46 | GD-1 | Gujarat | GJ | Western | 2026-07-24T05:47 | 2026-07-24T13:41 | 7.9 | 235 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 235 MW reported due to loss of evacuation path. | 27 GD-1 Gujarat 24-07-2026 05:47 24-07-2026 13:41 07:54 235 - 0.35% - 67764 55716 Complete outage of 220kV Khakharda S/S: At 05:47 Hrs/24-07-2026, 220KV Jamkhambaliya – Khakharda line tripped due to Y- phase to Earth fault. Generation loss of 235 MW reported due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220KV Jamkhambaliya – Khakharda | grid_india_gd/grid_events/2026-07-01
G00402 | 2026-07 | 47 | GD-1 | Gujarat | GJ | Western | 2026-07-24T06:46 | 2026-07-24T09:17 | 2.52 | 145 |  | FALSE | FALSE | FALSE | FALSE | FALSE | As this was the main evacuation line, the power flow on the 220 kV Nakhatrana–Dhedhiya inter-connecting line become zero, resulting in a generation loss of approximately 145 MW. | 28 GD-1 Gujarat 24-07-2026 06:46 24-07-2026 09:17 02:31 145 - 0.21% - 69914 58131 Complete outage of 220kV Nakhatrana S/S: 220 kV Bhuj-II–Nakatrana-1 line tripped at 06:46 hrs on 24.07.2026 from the Nakhatrana end due to an Y-E fault. As this was the main evacuation line, the power flow on the 220 kV Nakhatrana–Dhedhiya inter-connecting line become zero, resulting in a generation loss of approximately 145 MW. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj II-Nakhatrana | grid_india_gd/grid_events/2026-07-01
G00403 | 2026-07 | 48 | GD-1 | Gujarat | GJ | Western | 2026-07-24T15:16 | 2026-07-24T19:24 | 4.13 | 540 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of around ~540 MW has occurred due to loss of evacuation path. | 29 GD-1 Gujarat 24-07-2026 15:16 24-07-2026 19:24 04:08 540 - 0.77% - 69771 54790 Complete outage of 220kV Bhuj-II S/S: At 15:16 Hrs, 220kV Nakhatrana-Bhuj-II & 220kV Sitec-Bhuj-II both lines were tripped due to R-E fault. After patrolling, conductor snap observed on 220kV Nakhatrana- Bhuj-II line at Bhuj-II end. Generation loss of around ~540 MW has occurred due to loss of evacuation path. Tripping of following Elements: 1. 220kV Nakhatrana-Bhuj-II 2. 220kV Sitec-Bhuj-II | grid_india_gd/grid_events/2026-07-01
G00404 | 2026-07 | 49 | GD-1 | Gujarat | GJ | Western | 2026-07-24T23:19 | 2026-07-25T18:47 | 19.47 | 258 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 158 MW occurred due to the event At 23:47 Hrs /24-07-2026, 220 kV Bhuj- Kotda Madh S/C line tripped on B-E fault. | 30 GD-1 Gujarat 24-07-2026 23:19 25-07-2026 18:47 19:28 258 - 0.37% - 69147 60185 Complete outage of 220kV Naranpar & Kotda Madh S/S: At 23:19 Hrs /24-07-2026, 220 kV Bhuj- Naranpar S/C line tripped on B-E fault. Due to loss of evacuation path, 220kV Naranpar S/S went dark. Generation loss of 158 MW occurred due to the event At 23:47 Hrs /24-07-2026, 220 kV Bhuj- Kotda Madh S/C line tripped on B-E fault. Due to loss of evacuation path, 220kV Kotda Madh S/S went dark. Generation loss of 100 MW occurred due to the event. Tripping of following Elements: 1. 220 kV Bhuj- Naranpar S/C 2. 220 kV Bhuj- Kotda Madh S/C | grid_india_gd/grid_events/2026-07-01
G00405 | 2026-07 | 60 | GI-2 | Andhra Pradesh | AP | Southern | 2026-07-25T19:20 | 2026-07-25T19:45 | 0.42 | 1200 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GI-2 ANDHRA PRADESH 25-07-2026 19:20 25-07-2026 19:45 00:25 1200 0 2.11% 0.00% 56758.88 56315.73 Tripping of 400kV Bus-2 of 400kV Greenko PSP of GREENKO During antecedent conditions, Greenko Unit-1,3,4,5& 6 were in Generation mode. As per the reports submitted, When the system frequency reached 4 | 15 GI-2 ANDHRA PRADESH 25-07-2026 19:20 25-07-2026 19:45 00:25 1200 0 2.11% 0.00% 56758.88 56315.73 Tripping of 400kV Bus-2 of 400kV Greenko PSP of GREENKO During antecedent conditions, Greenko Unit-1,3,4,5& 6 were in Generation mode. As per the reports submitted, When the system frequency reached 49.5 Hz, all five units, generating approximately 1200 MW, tripped on under-frequency protection as Under frequency for the generator enabled at 49.5 Hz, 5 seconds even for generation mode which led to tripping of all the 5 no. of units running in generation mode. At the same time, B-G fault was observed in 400kV Greenko PSP Bus-2 due to breaker flahover in Unit-6. Immediately, 400kV Bus-2 BBP operated tripping all elements connected to 400kV Bus-2. Greenko - UNIT 1, Greenko - UNIT 3, Greenko - UNIT 4, Greenko - UNIT 5, Greenko - UNIT 6 | grid_india_gd/grid_events/2026-07-01
G00406 | 2026-07 | 61 | GI-2 | Andhra Pradesh | AP | Southern | 2026-07-26T01:46 | 2026-07-26T02:45 | 0.98 | 220 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GI-2 ANDHRA PRADESH 26-07-2026 01:46 26-07-2026 02:45 00:59 220 0 0.43% 0.00% 51377.88 51067.69 Tripping of 400kv Bus-1 of 400kv Greenko_PSP of GREENKO As per the reports submitted, the triggering incident was B-phase breaker flashover in Greenko Unit-6 while de paralleling the Unit. Immediately, | 16 GI-2 ANDHRA PRADESH 26-07-2026 01:46 26-07-2026 02:45 00:59 220 0 0.43% 0.00% 51377.88 51067.69 Tripping of 400kv Bus-1 of 400kv Greenko_PSP of GREENKO As per the reports submitted, the triggering incident was B-phase breaker flashover in Greenko Unit-6 while de paralleling the Unit. Immediately, 400kV Greenko Bus-1 BBP operated and all elements connected to the bus tripped. GREENKO_PSP - 400KV - Bus 1, 400KV-GREENKO_CPSS- GREENKO_PSP-2, 400KV/11KV GREENKO_PSP-ST-2, 400KV/18KV GREENKO_PSP-GT-7, 400KV/18KV GREENKO_PSP-GT-8, Greenko - UNIT 7, Greenko - UNIT 8 | grid_india_gd/grid_events/2026-07-01
G00407 | 2026-07 | 62 | GI-2 | Telangana | TG | Southern | 2026-07-27T00:06 | 2026-07-27T07:11 | 7.08 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-2 TELANGANA 27-07-2026 00:06 27-07-2026 07:11 07:05 0 0 0.00% 0.00% 55113.6 49712.7 Tripping of 765kV Bus-1 of 765kV Maheswaram SS of PGCIL SR-1 As per the reports submitted, the triggering incident was Y-G fault in 765kV Maheswaram Bus-1. A flashover occured in GIS chamber of CB hence 765kV B | 17 GI-2 TELANGANA 27-07-2026 00:06 27-07-2026 07:11 07:05 0 0 0.00% 0.00% 55113.6 49712.7 Tripping of 765kV Bus-1 of 765kV Maheswaram SS of PGCIL SR-1 As per the reports submitted, the triggering incident was Y-G fault in 765kV Maheswaram Bus-1. A flashover occured in GIS chamber of CB hence 765kV Bus-1 BBP operated and all main breakers connected to the bus tripped. MAHESHWARAM_PG - 765KV - Bus 1 | grid_india_gd/grid_events/2026-07-01
G00408 | 2026-07 | 50 | GD-1 | Gujarat | GJ | Western | 2026-07-27T04:03 | 2026-07-27T23:37 | 19.57 | 89 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Due to tripping of only evacuating line, it caused generation loss of around 89 MW. | 31 GD-1 Gujarat 27-07-2026 04:03 27-07-2026 23:37 19:34 89 - 0.13% - 70388 56800 Complete outage of 220kV Srijan Morjar S/S: At 04:03 hrs/27.07.2026, 220 kV Srijan – Bhuj-II Circuit-1 tripped due to Y-phase to earth fault. Due to tripping of only evacuating line, it caused generation loss of around 89 MW. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Srijan – Bhuj-II | grid_india_gd/grid_events/2026-07-01
G00409 | 2026-07 | 16 | GD-1 | Uttarakhand | UK | Northern | 2026-07-27T11:49 | 2026-07-27T12:40 | 0.85 | 107 | 125 | FALSE | FALSE | FALSE | FALSE | FALSE | vii)As per SCADA, generation loss of approx 107 MW was observed at Tanakpur(NH) and approx 125MW load loss was observed in UP control area. | 16 GD-1 Uttarakhand 27-07-2026 11:49 27-07-2026 12:40 00:51 107 125 0.15 0.15 73714 81854 i)Tanakpur(NHPC) has double main bus scheme at 220kV level. It comprises 3 X 31.42 MW of generation ii)During antecedent condition, all three units of Tanakpur were in running condition and generating approx 37 MW, 35 MW and 35 MW respectively (as per SCADA). iii)As per PMU, the sequence of events is as follows, a)At 11:49:44, overcurrent protection of all three units at Tanakpur picked up. b)At 11:49:48, R-Y-B three phase fault was sensed in zone-3 from Tanakpur in 220 kV Tanakpur(NH)-CBGanj(UP) (PG) Ckt. c)At 11:49:49, after ~1000 msec of sensing zone 3 fault, 220 kV Tanakpur(NH)-CBGanj(UP) (PG) Ckt tripped from Tanakpur end only (location of fault is yet to be shared). d)At the same time, all three units of Tanakpur tripped due to operation of overcurrent protection after ~5 sec delay. iv)During tripping of Unit-1, B-ph CB got stuck leading to Bus-1 LBB operation and tripping of 220kV Tanakpur(NH)-Sitarganj(PG) (PG) Ckt and 220/132kV 100 MVA ICT 1 at Tanakpur(NH). Thus, complete blackout occurred at 220 kV Tanakpur(NH). v)As per SCADA SOE, at the same time 220kV CB Ganj_1 - CB Ganj_2(UP) Ckt-1, 220kV Badaun - CB Ganj_2(UP) Ckt-1, 132kV Dohna - CB Ganj_2(UP) Ckt-1, 220/132kV ICT-1 at CB Ganj_2, and 132kV Meerganj - CB Ganj_2 (UP) Ckt-3 also tripped. As reported by SLDC UP, 132kV Aonla - CB Ganj(UP) Ckt-2 tripped during the same time due to broken conductor found at tower loc. no. 31. H | grid_india_gd/grid_events/2026-07-01
G00410 | 2026-07 | 15 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-07-27T20:18 | 2026-07-27T21:19 | 1.02 | 712 | 278 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 720 MW was observed at Salal(NH), and ~278MW load loss was observed in J&K control area. | 15 GD-1 Jammu and Kashmir 27-07-2026 20:18 27-07-2026 21:19 01:01 712 278 1.15 0.32 62058 86205 i)220kV Salal(NH) double main bus scheme. It comprises 6 X 115MW of generation. ii)During antecedent condition, Salal HPS was operating in bus split mode; all six 115 MW units of Salal HPS were in running condition and generating approx 120 MW each (as per SCADA). iii)As reported, at 20:18hrs, R-ph CB of 115 MW Unit-6 at Salal(NH) got opened due to maloperation of mechanical plunger system. Due to this pole discrepancy protection operated. Following pole discrepancy operation, the B-phase pole failed to open (stuck pole condition), leading to LBB protection operation in Bus-2 (Unit-6 was connected to Bus-2). iv)As reported, due to issue in hardware logic, LBB issued trip command to all bays connected to Bus-1 as well and complete blackout occurred at 220 kV Salal. v)As per PMU at Kishenpur(PG), no fault was observed. vi)As per SCADA, generation loss of approx 720 MW was observed at Salal(NH), and ~278MW load loss was observed in J&K control area. vii)As reported, the operating mechanism of the B-phase circuit breaker of Unit-6 has been replaced 1) 115 MW SALAL HPS - UNIT 6 2) 115 MW SALAL HPS - UNIT 1 3) 115 MW SALAL HPS - UNIT 2 4) 115 MW SALAL HPS - UNIT 3 5) 115 MW SALAL HPS - UNIT 4 6) 115 MW SALAL HPS - UNIT 5 7) 220 kV Salal(NH)-Jammu(PDD) (PG) Ckt-1 8) 220 kV Salal(NH)-Jammu(PDD) (PG) Ckt-2 9) 220 kV Kishenpur(PG)-Salal(NH) (PG) Ckt-1 10) 220 kV Kishenpur(PG)-Salal(NH) (PG) | grid_india_gd/grid_events/2026-07-01
G00411 | 2026-07 | 17 | GD-1 | Rajasthan | RJ | Northern | 2026-07-28T14:49 | 2026-07-28T16:02 | 1.22 | 911 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | vii)As per SCADA, Generation loss of ~238 MW at RSDCL-2(NTPC) and ~911MW dip in NR total solar was observed. | 17 GD-1 Rajasthan 28-07-2026 14:49 28-07-2026 16:02 01:13 911 0 1.30 0.00 70144 76257 i)220kV RSDCL-2(NTPC) has double main bus system. ii)Generation of 220kV RSDCL-2(NTPC) station evacuates through 220 kV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt. iii)During antecedent condition, 220kV RSDCL-2(NTPC) station was generating approx 238 MW (as per SCADA). iv)As reported, at 14:49hrs, 765 KV Bhadla-Bikaner (PG) Ckt-1 tripped due to R-Y phase to phase fault with fault current of 7.2kA and fault distance of 101KM from Bikaner(PG) end. v)At the same time, 220 kV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt tripped from RSDCL-2(NTPC) end only.As per DR, no fault was sensed by the relay hence maloperation is suspected. vi)As per PMU at Bikaner(PG), R-Y phase to phase fault was observed with fault clearing time of 80ms. vii)As per SCADA, Generation loss of ~238 MW at RSDCL-2(NTPC) and ~911MW dip in NR total solar was observed. 1) 765 kV Bhadla-Bikaner (PG) Ckt-1 2) 220 kV Bhadla_2 (PG)-RSDCL(PSS2)_SL_BHD2_PG (RSDCL) Ckt-1 | grid_india_gd/grid_events/2026-07-01
G00412 | 2026-07 | 51 | GD-1 | Madhya Pradesh | MP | Western | 2026-07-29T11:57 | 2026-07-29T14:20 | 2.38 | 120 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 120 MW. | 32 GD-1 Madhya Pradesh 29-07-2026 11:57 29-07-2026 14:20 02:23 120 - 0.17% - 71907 62395 Complete outage of 400 Gandhinagar S/S: At 11:57 hrs, Busbar protection operated at Gandhinagar TPS SS due to which 220kV bus-2 tripped. It led to tripping of 05 nos 220kV lines and GTPS (U#4) tripping. Generation loss of 120 MW. Due to tripping of all evacuating lines from Gandhinagar S/S, GD has occurred. Tripping of following Elements: 1. 220kV lines and GTPS (U#4) | grid_india_gd/grid_events/2026-07-01
G00413 | 2026-07 | 18 | GD-1 | Haryana | HR | Northern | 2026-07-29T17:57 | 2026-07-29T18:57 | 1 | 0 | 102 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GD-1 Haryana 29-07-2026 17:57 29-07-2026 18:57 01:00 0 102 0.00 0.13 61819 79080 i)220/132kV Charkhi Dardi (BBMB) S/s has double main bus scheme at 220kV level. ii)Under the antecedent system conditions, the 220 kV bus coupler was closed. 220 kV Charkhi Dadri(BB)–Khetri(RS)(BB) Ckt-1 and Ckt-2 we | 18 GD-1 Haryana 29-07-2026 17:57 29-07-2026 18:57 01:00 0 102 0.00 0.13 61819 79080 i)220/132kV Charkhi Dardi (BBMB) S/s has double main bus scheme at 220kV level. ii)Under the antecedent system conditions, the 220 kV bus coupler was closed. 220 kV Charkhi Dadri(BB)–Khetri(RS)(BB) Ckt-1 and Ckt-2 were open for loading management. However, the corresponding bus isolators remained connected to Bus-1. All other circuits were in service. iii)As reported by BBMB, at 17:57 hrs, due to a malfunction in the circuit breaker (CB), the Y-phase pole of the CB of the 220 kV Charkhi Dadri(BB)–Khetri(RS) (BB) Ckt-1 closed inadvertently while the earth switch was in the closed position, resulting in a Y-phase to earth fault. During the fault, the Y-phase pole of the CB remained stuck in the closed position. Consequently, LBB protection operated, leading to the tripping of all elements connected to Bus-1. iv)During the LBB operation, the bus coupler failed to open, resulting in the tripping of Bus-2 along with all the elements connected to it. v)Outage of both buses resulted in complete blackout of 220/132kV Charkhi Dadri s/s and load loss in Haryana control area. vi)As per PMU at Panchkula(PG), Y-N Phase to earth fault was observed with fault clearance time of ~320 msec. vii)As per SCADA, change in demand of approx 102 MW was observed in Haryana control area. 1) 220KV Bus 1 at Charkhi Dadri(BB) 2) 220KV Bus 2 at Charkhi Dadri(BB) 3) 220 KV Charkhi Dadri-Samaypur (BB) Ckt-1 4) 220 KV Bhiwani- | grid_india_gd/grid_events/2026-07-01
G00414 | 2026-07 | 63 | GI-2 | Andhra Pradesh | AP | Southern | 2026-07-29T19:33 | 2026-07-29T20:46 | 1.22 | 95 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 400KV/33KV ATP_RenewVyoman_PSS2-ICT-1, ATP_RenewVyoman_PSS2 - 400KV - Bus 2 Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD-I Sikkim 28-07-2026 10:54 28-07-2026 11:33 00:39 484 0 1.80% 0.00% 26834 27913 Prior to the disturbance, the 400 kV Rangpo–Teesta V Line-1 was | 18 GI-2 ANDHRA PRADESH 29-07-2026 19:33 29-07-2026 20:46 01:13 95 0 0.16% 0.00% 59189.23 56637.16 Tripping of 400kV Bus-2 of 400kV ATP_RenewVyoman_PSS2 of RENEW As per the reports submitted, the triggering incident was RYB fault in downstream 33kV feeder of 400kV ATP_RenewVyoman_PSS2. At the same time, 400kV/33kV ATP_RenewVyoman_PSS2 ICT-1 tripped on REF protection. As 400kV ATP_RenewVyoman_PSS2 Bus-2 of grid was connected through Tie breaker of the 400kV/33kV ATP_RenewVyoman_PSS2 ICT-1, tripping of the ICT led to tripping of 400kV Bus-2 of 400kV ATP_RenewVyoman_PSS2. 400KV/33KV ATP_RenewVyoman_PSS2-ICT-1, ATP_RenewVyoman_PSS2 - 400KV - Bus 2 Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD-I Sikkim 28-07-2026 10:54 28-07-2026 11:33 00:39 484 0 1.80% 0.00% 26834 27913 Prior to the disturbance, the 400 kV Rangpo–Teesta V Line-1 was under outage. The generation from Teesta V Units 1, 2, and 3 was around 484 MW, which was being evacuated through the 400 kV Rangpo–Teesta V Line-2. At 10:54 Hrs on 28.07.2026, during the synchronization of the 400 kV Rangpo–Teesta V Line-1 at Teesta V S/s, the busbar protection for both Main Bus-1 and Main Bus-2 operated spuriously due to the reverse CT polarity in bus bar protection scheme. As a result of the busbar protection operation on both buses, all connected elements at 400 kV Teesta V S/s got tripped, causing | grid_india_gd/grid_events/2026-07-01
G00415 | 2026-07 | 54 | GD-1 | Gujarat | GJ | Western | 2026-07-30T13:41 | 2026-07-30T19:15 | 5.57 | 15 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 35 GD-1 Gujarat 30-07-2026 13:41 30-07-2026 19:15 05:34 15 - 0.02% - 64458 60311 Complete outage of 220kV Nanavalka S/S: At 13:41 Hrs, 220 KV Bhuj - Nanavalka S/C tripped on Bph-E fault leading to generation loss of 15 MW due to tripping of only evacuation path. | 35 GD-1 Gujarat 30-07-2026 13:41 30-07-2026 19:15 05:34 15 - 0.02% - 64458 60311 Complete outage of 220kV Nanavalka S/S: At 13:41 Hrs, 220 KV Bhuj - Nanavalka S/C tripped on Bph-E fault leading to generation loss of 15 MW due to tripping of only evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 KV Bhuj - Nanavalka S/C | grid_india_gd/grid_events/2026-07-01
G00416 | 2026-07 | 55 | GD-1 | Gujarat | GJ | Western | 2026-07-30T16:44 | 2026-07-30T17:44 | 1 | 62 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 36 GD-1 Gujarat 30-07-2026 16:44 30-07-2026 17:44 01:00 62 - 0.08% - 75023 64204 Complete outage of 220kV Shajapur S/S: At 16:44 Hrs/30-07-2026, 220kV Shajapur U7 -Shajapur U6 line tripped due to over current relay operation at 33 KV bay, generation loss of 62 MW due to loss of evacuation path . | 36 GD-1 Gujarat 30-07-2026 16:44 30-07-2026 17:44 01:00 62 - 0.08% - 75023 64204 Complete outage of 220kV Shajapur S/S: At 16:44 Hrs/30-07-2026, 220kV Shajapur U7 -Shajapur U6 line tripped due to over current relay operation at 33 KV bay, generation loss of 62 MW due to loss of evacuation path . Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Shajapur Unit-6 (Burley) - Shajapur Unit-7 (Dehripal) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 TAMILNADU 05-07-2026 10:34 05-07-2026 11:32 00:58 0 18 0.00% 0.04% 56273.56 51362.28 Tripping of 230kV Bus-1 Sriperambadur of TANTRANSCO and Complete Outage of 230kV Hyundai SS 230kV Hyundai station was radially fed from 230kV Bus-1 Sriperambadur SS. 230 kV Bus-1 and Bus-2 at Sriperambadur were in service and operating in split bus condition, with the bus coupler in the open condition. The triggering incident is the Y-G fault on the Hyundai feeder and led to the tripping of the line. Further jumper conductor failed between the CT and the circuit breaker snapped towards the CT side and Local Breaker Backup (LBB) operated in Bus-1 and all elements connected to Tripping of 230kV Bus-1 Sriperambadur of TANTRANSCO and with the tripping of 230kV Sriperambadur-Hyundai led to the complete outage of 230kV Hyundai station SRIPERUMBADUR_TN - 230KV - Bus 1, 230KV-HYUNDA | grid_india_gd/grid_events/2026-07-01
G00417 | 2026-07 | 52 | GD-1 | Gujarat | GJ | Western | 2026-07-30T21:32 | 2026-08-04T12:25 | 110.88 | 44 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 44 MW occurred due to loss of evacuation path. | 33 GD-1 Gujarat 30-07-2026 21:32 04-08-2026 12:25 110:53 44 - 0.06% - 76673 62829 Complete outage of 220kV Devsar S/S: At 21:32 Hrs on 30-07-2026, 220kV Bhuj–Devsar line tripped due to Bph-E fault. Generation loss of 44 MW occurred due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220 kV Bhuj-Devsar-1 S/C | grid_india_gd/grid_events/2026-07-01
G00418 | 2026-07 | 53 | GD-1 | Gujarat | GJ | Western | 2026-07-30T21:32 | 2026-07-30T22:16 | 0.73 | 37 |  | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 37 MW occurred due to loss of evacuation path. | 34 GD-1 Gujarat 30-07-2026 21:32 30-07-2026 22:16 00:44 37 - 0.05% - 76673 62829 Complete outage of 220kV Gadhsisa S/S: At 21:32 Hrs on 30-07-2026, 220kV Bhuj–Gadhsisa line tripped at Gadhsisa end due to Bph-E fault. Generation loss of 37 MW occurred due to loss of evacuation path. Due to tripping of only evacuating line GD occurred. Tripping of following Elements: 1. 220kV Bhuj–Gadhsisa | grid_india_gd/grid_events/2026-07-01
G00419 | 2026-07 | 19 | GD-1 | Rajasthan | RJ | Northern | 2026-07-31T15:23 | 2026-07-31T17:14 | 1.85 | 374 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 99MW at SRI8PL(IP) & approx 275 MW at SRI9PL(IP) was observed. | 19 GD-1 Rajasthan 31-07-2026 15:23 31-07-2026 17:14 01:51 374 0 0.51 0.00 73626 80697 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) was generating approx 99MW and 275MW respectively (as per SCADA). iii)As reported, at 15:23 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped. As per DR, no fault was observed; however, R-phase differential protection operated. This led to complete blackout of 400kV Serentica 8 & 9 (IP) S/s. iv)At the same time, 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt also tripped (exact reason and nature of protection operated is yet to be shared). v)As per PMU at Fatehgarh3(IP), no fault was observed. vi)As per SCADA, generation loss of approx 99MW at SRI8PL(IP) & approx 275 MW at SRI9PL(IP) was observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt 2) 400 KV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt-1 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-07-01
G00420 | 2026-08 | 42 | GI-1 | Kerala | KL | Southern | 2026-08-01T02:19 | 2026-08-01T04:26 | 2.12 | 0 | 0 | FALSE | FALSE | TRUE | FALSE | TRUE | 6 GI-1 KERALA 01-08-2026 02:19 01-08-2026 04:26 02:07 0 0 0.00% 0.00% 4987 7 49226 Tripping of 220kV Bus-2 at Edamon SS of KSEB As per the reports submitted the 220kV Edamon-Pothencode-2 and 220kV Sabarigiri-Edamon-2 tripped prior to the event at 02:09 Hrs (R-G fault) and 02:12 Hrs (Y-B fault) respe | 6 GI-1 KERALA 01-08-2026 02:19 01-08-2026 04:26 02:07 0 0 0.00% 0.00% 4987 7 49226 Tripping of 220kV Bus-2 at Edamon SS of KSEB As per the reports submitted the 220kV Edamon-Pothencode-2 and 220kV Sabarigiri-Edamon-2 tripped prior to the event at 02:09 Hrs (R-G fault) and 02:12 Hrs (Y-B fault) respectively. It is suspected due to these trippings, dielectric insulation breakdown and internal arcing initiated in the Y-phase of the 220kV Sabarigiri- Edamon-2 Hybrid PASS unit resulting in a solid Y-G bus fault and instantaneously tripped all elements connected to Bus - 2 at Edamon end. This led to tripping of 220kV Bus-2 at Edamon SS of KSEB. EDAMON - 220KV - Bus 2, 220KV-EDAMON-EDAPPON-1, 220KV-TIRUNELVELI-EDAMON-1 | grid_india_gd/grid_events/2026-08-01
G00421 | 2026-08 | 43 | GI-1 | Telangana | TG | Southern | 2026-08-01T15:26 | 2026-08-01T17:46 | 2.33 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 7 GI-1 TELANGANA 01-08-2026 15:26 01-08-2026 17:46 02:20 0 0 0.00% 0.00% 6 1606 64108 Tripping of 220kV Bus-1 of 220kV Kamalapuram SS of TGTRANSCO As per the reports, a fault on the LV side of 220/11 kV Station Transformer-2 led to malfunctioning of the 220 kV Busbar-1 protection, resulting in tripp | 7 GI-1 TELANGANA 01-08-2026 15:26 01-08-2026 17:46 02:20 0 0 0.00% 0.00% 6 1606 64108 Tripping of 220kV Bus-1 of 220kV Kamalapuram SS of TGTRANSCO As per the reports, a fault on the LV side of 220/11 kV Station Transformer-2 led to malfunctioning of the 220 kV Busbar-1 protection, resulting in tripping of all breakers connected to Busbar-1. Subsequently, ICT-1 and ICT-3 tripped on the 96 relay signal, causing the outage of 220 kV Busbar-1 at 400 kV Kamalapuram Substation KAMALAPURAM - 220KV - Bus 1, 400KV/220KV KAMALAPURAM-ICT-1, 400KV/220KV KAMALAPURAM-ICT- 3 | grid_india_gd/grid_events/2026-08-01
G00422 | 2026-08 | 26 | GD-1 | Gujarat | GJ | Western | 2026-08-01T20:53 | 2026-08-02T05:58 | 9.08 | 123 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 123 MW occurred at 220kV Naranpar S/S due to loss of evacuation path and station went dark. | 2 GD-1 Gujarat 01-08-2026 20:53 02-08-2026 05:58 09:05 123 0 0.16% 0.00% 7 5581 61622 Complete outage of 220 kV Naranpar S/S: At 20:53 Hrs /01-08-2026, 220 kV Bhuj- Naranpar S/C line tripped on B-phase to Earth fault. Generation loss of 123 MW occurred at 220kV Naranpar S/S due to loss of evacuation path and station went dark. Tripping of following Elements: 1 220 kV Bhuj-Roha-Naranpar 2 220 kV Roha-Naranpar ICT-1 3 220 kV Roha-Naranpar ICT-2 | grid_india_gd/grid_events/2026-08-01
G00423 | 2026-08 | 44 | GI-1 | Kerala | KL | Southern | 2026-08-02T09:02 | 2026-08-02T10:04 | 1.03 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 8 GI-1 KERALA 02-08-2026 09:02 02-08-2026 10:04 01:02 0 0 0.00% 0.00% 5899 8 61267 Tripping of 220kV Bus-1 & Bus-3 of 220kV Pothencode SS of KSEB At 220kV Pothencode SS, Bus-1 and 3 are permanently coupled. As per the reports submitted, the triggering incident was R phase disc insulator flashover in | 8 GI-1 KERALA 02-08-2026 09:02 02-08-2026 10:04 01:02 0 0 0.00% 0.00% 5899 8 61267 Tripping of 220kV Bus-1 & Bus-3 of 220kV Pothencode SS of KSEB At 220kV Pothencode SS, Bus-1 and 3 are permanently coupled. As per the reports submitted, the triggering incident was R phase disc insulator flashover in the Bus 1 side of 220 kV Bus coupler in the 220 kV Pothencode substation. As the fault was in the Bus 1 side of the bus coupler, differential protection of Busbar 1 operated and tripped all the elements connected to 220kV Bus-1 tripped and led to the Tripping at 220kV Bus-1 and 3 at Pothencode SS of KSEB 220KV-POTHENCODE-TRIVANDRUM-1, 220KV- POTHENCODE-TRIVANDRUM-3, 220KV-EDAMON- POTHENCODE-2, POTHENCODE - 220KV - Bus 1, POTHENCODE - 220KV - Bus 3 | grid_india_gd/grid_events/2026-08-01
G00424 | 2026-08 | 27 | GD-1 | Goa | GA | Western | 2026-08-02T12:32 | 2026-08-02T16:00 | 3.47 | 0 | 64 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GD-1 Goa 02-08-2026 12:32 02-08-2026 16:00 03:28 0 64 0.00% 0.11% 64002 5 5890 Complete outage of 220 kV Xeldem S/S: At 12:32 Hrs / 02-08-2026, 220 kV Xeldem (Sterlite) Bus-2 tripped on account of a malfunction of the Gas Density Monitor (GDM) of G9-5 Y-phase Stage-3 gas zone, which operated in Ba | 3 GD-1 Goa 02-08-2026 12:32 02-08-2026 16:00 03:28 0 64 0.00% 0.11% 64002 5 5890 Complete outage of 220 kV Xeldem S/S: At 12:32 Hrs / 02-08-2026, 220 kV Xeldem (Sterlite) Bus-2 tripped on account of a malfunction of the Gas Density Monitor (GDM) of G9-5 Y-phase Stage-3 gas zone, which operated in Bay No. 209 (a future/spare bay of Verna-2 line). All elements connected to Bus-2, namely 220 kV Xeldem–Xeldem-2 line and 400/220 kV ICT-2, tripped along with it. A load loss of 64 MW was reported in the Goa control area. Tripping of following Elements: 1 220 kV Xeldem(Sterlite) Bus-2 2 220 kV Xeldem(Sterlite)–Xeldem(GOA) Ckt-2 3 400/220 kV ICT-2 | grid_india_gd/grid_events/2026-08-01
G00425 | 2026-08 | 1 | GD-1 | Rajasthan | RJ | Northern | 2026-08-02T15:01 | 2026-08-02T15:44 | 0.72 | 425 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 425MW at SRI8PL(IP) & SRI9PL(IP) was observed. | 1 GD-1 Rajasthan 02-08-2026 15:01 02-08-2026 15:44 00:43 425 0 0.65% 0.00 % 65023 80183 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, 400kV Serentica 8 & 9 (IP) were generating approx 425 MW (as per SCADA). iii)As reported, at 15:01 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped. As per DR, no fault was observed; however, R-phase differential protection operated. iv)This led to complete blackout of 400kV SRI8PL(IP) & SRI9PL(IP) S/s. v)As per PMU at Fatehgarh3(IP), no fault was observed. vi)As per SCADA, generation loss of approx 425MW at SRI8PL(IP) & SRI9PL(IP) was observed. 1) 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt | grid_india_gd/grid_events/2026-08-01
G00426 | 2026-08 | 25 | GD-1 | Gujarat | GJ | Western | 2026-08-02T21:01 | 2026-08-02T23:28 | 2.45 | 0 | 120 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 Gujarat 02-08-2026 21:01 02-08-2026 23:28 02:27 0 120 0.00% 0.23% 6 8094 52678 Complete outage of 220 kV Sarigram S/S: At 21:01 hrs / 02-08-2026, 220 kV Sarigram-Vapi(GJ)-1 S/C tripped on R-E Fault. Due to delayed clearance of fault, after around 400 msec, 220 kV Sarigram- Tarapur1&2-1 S/C tr | 1 GD-1 Gujarat 02-08-2026 21:01 02-08-2026 23:28 02:27 0 120 0.00% 0.23% 6 8094 52678 Complete outage of 220 kV Sarigram S/S: At 21:01 hrs / 02-08-2026, 220 kV Sarigram-Vapi(GJ)-1 S/C tripped on R-E Fault. Due to delayed clearance of fault, after around 400 msec, 220 kV Sarigram- Tarapur1&2-1 S/C tripped on R-E fault in Zone-2 (from Tarapur1&2 end only), no relay indication reported by Sarigram End (GETCO). Simultaneously, 220 kV Sarigram-Bhilad-1 S/C tripped on B-E fault in Zone-1 at Bhilad end. Load loss of 120 MW occurred at Sarigram region as reported by Gujarat SLDC. Tripping of following Elements: 1 220 kV Sarigam- Vapi(GJ)-1 S/C 2 220 kV Sarigam-Bhilad-1 S/C 3 220 kV Sarigam-Tarapur1&2-1 S/C 4 220/66 kV Sarigam ICT-1 (160 MVA) 5 220/66 kV Sarigam ICT-2 (160 MVA) 6 220/66 kV Sarigam ICT-3 (160 MVA) 7 220 kV Sarigam-Tarapur1&2-1 S/C 8 220/66 kV 160 MVA Sarigam ICT 1 | grid_india_gd/grid_events/2026-08-01
G00427 | 2026-08 | 45 | GI-2 | Andhra Pradesh | AP | Southern | 2026-08-03T00:17 | 2026-08-03T02:13 | 1.93 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-2 ANDHRA PRADESH 03-08-2026 00:17 03-08-2026 02:13 01:56 0 0 0.00% 0.00% 52973 49123 Tripping of 400kV BUS-3 at 400kV NTPC SIMHADRI of NTPC During overhauling of unit 4 of the Simhadri generating station, generator lockout relay manually operated but due to some CB coil failure R phase of 428 m | 9 GI-2 ANDHRA PRADESH 03-08-2026 00:17 03-08-2026 02:13 01:56 0 0 0.00% 0.00% 52973 49123 Tripping of 400kV BUS-3 at 400kV NTPC SIMHADRI of NTPC During overhauling of unit 4 of the Simhadri generating station, generator lockout relay manually operated but due to some CB coil failure R phase of 428 main CB failed to open and due to this condition Local breaker back up protection triggered and opened all the breakers connected with Bus 3 which led to tripping of 400kV Bus-3 of 400kV NTPC SIMHADRI of NTPC SIMHADRI - 400KV - Bus 3 | grid_india_gd/grid_events/2026-08-01
G00428 | 2026-08 | 2 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-08-03T11:52 | 2026-08-03T12:22 | 0.5 | 0 | 290 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GD-1 Jammu & Kashmir 03-08-2026 11:52 03-08-2026 12:22 00:30 0 290 0.00% 0.35% 72341 82033 i)220/132kV Barn(JK) is connected with 400/220kV Kishenpur(PG) through 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)During antecedent condition, 400/220kV 2*315 MVA ICT-1 & 2 were already runni | 2 GD-1 Jammu & Kashmir 03-08-2026 11:52 03-08-2026 12:22 00:30 0 290 0.00% 0.35% 72341 82033 i)220/132kV Barn(JK) is connected with 400/220kV Kishenpur(PG) through 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)During antecedent condition, 400/220kV 2*315 MVA ICT-1 & 2 were already running over its rated capacity i.e., carrying ~323 MVA each (~265MW and ~184MVAR) and was in increasing trend, and 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 were carrying ~156 MW each (as per SCADA). iii)As reported, at 11:52 hrs, 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 tripped due to operation of SPS at Kishenpur(PG). As per SPS logic at 400/220kV Kishenpur(PG), if loading of any 315MVA ICT at Kishenpur(PG) exceeds 110% of the rated capacity for 3 secs, 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) D/C shall trip. iv)As 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) D/C was the only 220kV source for 220/132kV Barn(JK) s/s, tripping of these circuits resulted in complete blackout of 220/132kV Barn(JK) s/s. v)As per PMU at Kishenpur(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 290 MW was observed in J&K control area. 1) 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 2) 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-2 | grid_india_gd/grid_events/2026-08-01
G00429 | 2026-08 | 28 | GD-1 | Gujarat | GJ | Western | 2026-08-04T05:31 | 2026-08-04T13:50 | 8.32 | 122 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, Generation loss of 122 MW reported. | 4 GD-1 Gujarat 04-08-2026 05:31 04-08-2026 13:50 08:19 122 0 0.17% 0.00% 7 1014 62208 Complete outage of 220 kV Khakharda S/S:: At 05:31 Hrs/04-08-2026, 220KV Jamkhambaliya – Khakharda line tripped due to Y- phase to Earth fault. Due to loss of evacuation path, Generation loss of 122 MW reported. Tripping of following Elements: 1 220KV Jamkhambaliya – Khakharda line 2 220/33 KV ICT-1 3 220/33 KV ICT-2 | grid_india_gd/grid_events/2026-08-01
G00430 | 2026-08 | 4 | GI-2 | Haryana | HR | Northern | 2026-08-04T15:32 | 2026-08-04T16:24 | 0.87 | 0 | 316 | FALSE | FALSE | FALSE | FALSE | FALSE | 4 GI-2 Haryana 04-08-2026 15:32 04-08-2026 16:24 00:52 0 316 0.00% 0.43% 6 6583 73445 i)400/220 kV Panipat (BBMB) Substation has a double main bus system at the 220 kV level. Bus-2 is provided with a bus sectionalizer. Bus Coupler-1 connects the LHS of Bus-2 with Bus-1, while Bus Coupler-2 connects | 4 GI-2 Haryana 04-08-2026 15:32 04-08-2026 16:24 00:52 0 316 0.00% 0.43% 6 6583 73445 i)400/220 kV Panipat (BBMB) Substation has a double main bus system at the 220 kV level. Bus-2 is provided with a bus sectionalizer. Bus Coupler-1 connects the LHS of Bus-2 with Bus-1, while Bus Coupler-2 connects the RHS of Bus-2 with Bus-1. ii)Under the antecedent conditions, 400/220 kV, 450 MVA ICT-1 was connected to Bus-1, while 400/220 kV, 500 MVA ICT-2 was connected to Bus-2 (RHS). Both bus couplers and the bus sectionalizer were in service; hence, the ICTs were operating in parallel. 220 KV Panipat(BB)-Chajpur(HV) (HVPNL) Ckt-1, 220 KV PanipatTH(HV)-Panipat(BB) (HVPNL) Ckt-1&3, 220 KV Narela(DV)-Panipat(BB) (HVPNL) Ckt-1&3 and 220 KV Panipat-Dhulkote (BB) Ckt-1 were connected to Bus-1. 220 KV Panipat(BB)-Chajpur(HV) (HVPNL) Ckt-2 and 220 KV PanipatTH(HV)-Panipat(BB) (HVPNL) Ckt-4 were connected to Bus-2(LHS). 220 KV Narela(DV)- Panipat(BB) (HVPNL) Ckt-2, 220 kV Panipat (BB)–Charkhi Dadri (BB) Ckt-1, 220 kV Panipat TH (HV)–Panipat (BB) (HVPNL) Ckt-2, 220 KV Panipat-Dhulkote (BB) Ckt-2, and 220 KV Panipat-Kurukshetra Ckt were connected to Bus-2(RHS) iii)As reported, at 15:24 hrs, 220 kV Bus Coupler-2 was hand-tripped after sparking was observed at the Bus-1 isolator of the bus coupler. iv)At 15:29 hrs, the bus sectionalizer tripped on earth-fault protection. As a result, ICT-1 & 2 got split and ICT-1 started feeding Bus-1 & Bus-2 (LHS), while ICT-2 started feeding Bus-2 (RHS). Consequen | grid_india_gd/grid_events/2026-08-01
G00431 | 2026-08 | 3 | GI-2 | Himachal Pradesh | HP | Northern | 2026-08-04T23:18 | 2026-08-05T00:38 | 1.33 | 550 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 550MW at Nathpa Jhakri and 150 MW at Rampur HEP were observed. | 3 GI-2 Himachal Pradesh 04-08-2026 23:18 05-08-2026 00:38 01:20 550 0 0.90% 0.00% 61203 79210 i)400kV Nathpa Jhakri(SJVN) and 400kV Rampur (SJVN) have double main bus scheme. Each comprises of 6 units of 250 MW and 68.67 MW respectively. ii)During antecedent condition, all six 250 MW units of Nathpa Jhakri and all six 68.67 MW units of Rampur were in running condition and generating approx 275 MW and 75 MW each respectively (as per SCADA). iii)As reported, at 23:18 hrs, an inadvertent SPS signal of case-3 of SPS scheme named “SPS for reliable evacuation of power from N. Jhakri, Rampur, Karcham Wangtoo, Sawra Kuddu, Baspa, Sorang and Naitwar Mori HEP” was generated at Nat hpa Jhakri HEP and this led to tripping of two units (Unit-3 & 5) at Nathpa Jhakri HEP. iv)Due to tandem operation logic, after tripping of two units at Nathpa Jhakri, two units (Unit-3 & 5) at Rampur HEP also tripped. v)As per PMU at Nallagarh(PG), no fault was observed in the system. vi)As per SCADA, generation loss of approx 550MW at Nathpa Jhakri and 150 MW at Rampur HEP were observed. 1) 250 MW Nathpa-Jhakri HPS - Unit 3 2) 250 MW Nathpa-Jhakri HPS - Unit 5 3) 68.67 MW Rampur HEP - Unit 3 4) 68.67 MW Rampur HEP - Unit 5 | grid_india_gd/grid_events/2026-08-01
G00432 | 2026-08 | 29 | GD-1 | Gujarat | GJ | Western | 2026-08-05T05:56 | 2026-08-05T21:54 | 15.97 | 190 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 145 MW occurred at 220KV Chugger (Sitac) due to loss of evacuation path. | 5 GD-1 Gujarat 05-08-2026 05:56 05-08-2026 21:54 15:58 190 0 0.25% 0.00% 7 4687 63403 Complete outage of 220 kV Chugger(Sitac) S/S:: At 05:56hrs/05.08.2026, 220 kV Bhuj-II-Chugger (Sitac) S/C line tripped on R-phase-Earth fault. Generation loss of 145 MW occurred at 220KV Chugger (Sitac) due to loss of evacuation path. Tripping of following Elements: 1 220 kV BhujII-Sitac/Chugger 4 220 kV Sitac/Chugger ICT-1 5 220 kV Sitac/Chugger ICT-2 | grid_india_gd/grid_events/2026-08-01
G00433 | 2026-08 | 5 | GD-1 | Himachal Pradesh | HP | Northern | 2026-08-06T06:58 | 2026-08-06T07:38 | 0.67 | 210 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 5 GD-1 Himachal Pradesh 06-08-2026 06:58 06-08-2026 07:38 00:40 210 0 0.37% 0.00% 57381 64397 i)Generation of AD Hydro HEP (2*96 MW) evacuates through 220kV AD Hydro-Nallagarh line (~175km) and 220kV AD Hydro-Phozal line(~14km)--> 220kV Phozal-Nallagarh Line. Both the lines are on same tower. There | 5 GD-1 Himachal Pradesh 06-08-2026 06:58 06-08-2026 07:38 00:40 210 0 0.37% 0.00% 57381 64397 i)Generation of AD Hydro HEP (2*96 MW) evacuates through 220kV AD Hydro-Nallagarh line (~175km) and 220kV AD Hydro-Phozal line(~14km)--> 220kV Phozal-Nallagarh Line. Both the lines are on same tower. There is LILO portion a t 220/33kV Phozal in second line. ii)During antecedent condition, weather condition was inclement (heavy rain) and 96 MW Unit-1 & 2 at AD Hydro HEP(IP) were generating approx 210 MW. 220kV AD Hydro-Nallagarh line was carrying ~228 MW and 220kV AD Hydro-Phozal line was not in service. iii)As reported at 06:58 hrs, 6:58:40.637 hrs, a B-N fault occurred on the 220 kV AD Hydro–Nalagarh (PG) (ADHPL) Circuit-1, resulting Zone-1 distance protection operation. Consequently, the B-phase Circuit Breaker (CB) at the AD Hydro end tripped. Auto Reclosure (AR) operated successfully at the A D Hydro end. However, during the AR sequence, the Circuit Breaker at the Nalagarh end failed to rec lose. As a result, the Pole Discrepancy (PD) operated, leading to a three-pole tripping of the Circuit Breaker at AD Hydro end. iv)As per PMU at Nalagarh end & DR of AD Hydro end, B-N fault (at 06:58:40.640 hrs) in Z-1 with successful A/R followed by 3-ph tripping after successful A/R is observed. v)With the tripping of both the evacuating lines, 96 MW Unit-1 and Unit-2 at AD Hydro HEP (generating ~210 MW) tripped due to loss of evacuation path. vi)As per SCADA plot of AD Hydro HEP generation, | grid_india_gd/grid_events/2026-08-01
G00434 | 2026-08 | 7 | GD-1 | Rajasthan | RJ | Northern | 2026-08-06T14:58 | 2026-08-06T19:59 | 5.02 | 262 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 262MW at SRI9PL(IP) was observed. | 7 GD-1 Rajasthan 06-08-2026 14:58 06-08-2026 19:59 05:01 262 0 0.37% 0.00 % 70781 69056 i)Generation of 400kV Serentica 8 & 9 (IP) evacuates through 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt. ii)During antecedent condition, there was no generation at Serentica8 as 400kV SRI8&26PL_Pooling_SL_Ftg3-SRI9PL_SL_Ftg3 (Serentica_RI8PL) Ckt was tripped on 02-Aug- 26 at 15:01 hrs and was under outage. 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt was carrying ~262 MW (as per SCADA). iii)As reported, at 14:58 hrs, 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt tripped on maloperation of differential protection. As per DR of Fatehgarh3(PG) end, no fault was observed; however, B-ph trip f ollowed by 3-ph trip is observed. iv)Due to tripping of 400 KV Fatehgarh_III(PG)-SRI9PL_SL_FTG3 (SERENTICA_RI9PL) Ckt, complete blackout occurred at 400kV SRI9PL(IP) S/s. v)As per PMU at Fatehgarh3(IP), no fault was observed. vi)As per SCADA, generation loss of approx 262MW at SRI9PL(IP) was observed. vii)As per details received from Fatehgarh3(PG), upon joint review, the issue was identified as a configuration mismatch in the line differential protection scheme (Hitachi Energy RED670 relay) between POWERGRID and Serentica ends. After verification of the protection scheme and current publishing configuration at the Serentica end, the root cause was identified, and the necessary configuration corr ections were implemented at the POWERGRID end. The issue h | grid_india_gd/grid_events/2026-08-01
G00435 | 2026-08 | 6 | GD-1 | Delhi | DL | Northern | 2026-08-06T18:05 | 2026-08-06T18:22 | 0.28 | 150 | 204 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, generation loss of approx 150MW occurred at Pragati Gas Turbines. | 6 GD-1 Delhi 06-08-2026 18:05 06-08-2026 18:22 00:17 150 204 0.27% 0.29% 5 6500 69771 i)220kV Pragati(PPCL), 220kV IPPOS(DTL) & 220kV Patparganj(DTL) have a double main bus scheme at 220kV level. ii)During the antecedent condition, the 220 kV Pragati and 220 kV Patparganj substations were operating in split-bus mode. At Pragati S/S, Unit-2, Unit-3, and 220 kV Pragati–IPPOS Ckt 1&2 were connected to Bus-1. At Patparganj S/S, the 220 kV Patparganj–IPPOS Ckt-1 & Ckt-2, 220 kV Patparganj–Geeta Colony (DTL) Ckt-2, and 220/33 kV ICT-1 & ICT-3 were connected to Bus-2. The 220 kV Patparganj–Geeta Colony (DTL) Ckt-1 was under shutdown. 220 kV Patparganj–Geeta Colony (DTL) Ckt-2 was supplying the local load of Patparganj S/S as well as the load of IPPOS S/S. Pragati Gas Turbine Units-2 and 3 were generating approx 150 MW in total and supplying the IPPOS S/S load. iii)As reported, at 18:05 hrs, 220kV Patparganj-Geeta Colony(DTL) Ckt-2 tripped on differential protection operation due to a Y-B phase-to-phase fault; the fault was sensed in zone 1 from Patparganj end with fault current of 2kA & 2.3kA from Patparganj end and 12.78kA & 12.55kA from Geeta Colony end. iv)At the same time, two running units of Pragati Gas Turbines (Unit-2 and Unit-3) also tripped (reason for tripping of generating units is yet to be shared). v)As Pragati and Patparganj were the only sources for IPPOS and were operating in split-bus mode, these trippings resulted in a blackout at 220kV IPPOS (DTL). vi)As per PMU | grid_india_gd/grid_events/2026-08-01
G00436 | 2026-08 | 30 | GD-1 | Maharashtra | MH | Western | 2026-08-07T02:16 | 2026-08-07T06:39 | 4.38 | 81 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 81.37 MW occurred at Tandulwadi (Serentica) WPP as a result. | 6 GD-1 Maharashtra 07-08-2026 02:16 07-08-2026 06:39 04:23 81 0 0.11% 0.0 0% 73522 59991 Complete outage of 220 kV Tandulwadi S/S: At 02:16 hrs on 07-08-2026, 220/33 kV ICT-1 and ICT-2 at 220 kV Tandulwadi (Serentica/SRI4PL) Wind Power Plant (radially connected with 220 kV Kallam) tripped on operation of 87T Transformer Differential Protection, simultaneously with a Y Phase-to-Earth fault on the 400 kV Parli-Kallam-2 line. Generation loss of 81.37 MW occurred at Tandulwadi (Serentica) WPP as a result. Tripping of following Elements: 1. 220 kV Tandulwadi ICT-01 2. 220 kV Tandulwadi ICT-02 | grid_india_gd/grid_events/2026-08-01
G00437 | 2026-08 | 8 | GD-1 | Haryana | HR | Northern | 2026-08-08T17:46 | 2026-08-08T18:00 | 0.23 | 0 | 396 | FALSE | FALSE | FALSE | FALSE | FALSE | iii)As reported by INDIGRID, at 17:46 hrs, while taking 220kV Bus-2 in service, bus isolator failed which further led to failu re of associated GIS compartment. | 8 GD-1 Haryana 08-08-2026 17:46 08-08-2026 18:00 00:14 0 396 0.00% 0.59% 5 3536 67653 i)400/220KV Sohna Road(GPTL) Sub-station has one & half breaker scheme at 400kV level and double main bus system at 220kV level. ii)During antecedent condition, 400/220kV 500 MVA ICT-1 & 2 at Sohna Road(GPTL) were carrying ~171 MW & ~173 MW respectively. 220kV Bus-2 at Sohna Road(GPTL) was taken under shutdown at 11:03AM on 08.08.2026 for scheduled maintenance work. iii)As reported by INDIGRID, at 17:46 hrs, while taking 220kV Bus-2 in service, bus isolator failed which further led to failu re of associated GIS compartment. Subsequently, 400/220kV ICT-1 & 2 also got fired and tripped on differential, OSR and PRD protection operation. Both the ICTs failed due to the fire incident. Exact location and nature of fault yet to be received from INDI GRID. iv)As reported by SLDC-HR, 220 KV Sohna Road (GPTL)-Badshahpur(HV) (HVPNL) D/C and 220 KV Sohna Road (GPTL)- Sec69 Gurgaon (HV) (HVPNL) D/C also tripped from remote end in Z-2 on Y-N fault. v)As per PMU at Gurgaon(PG), Y-N phase to earth fault with delayed clearance of ~660 msec is observed. vi)Further, between 18:27 hrs-18:41 hrs all the remaining 220kV & 400kV elements connected at Sohna Road(GPTL) were manually opened due to safety concern. vii)Load of Sec69 Gurgaon(HR) was affected during the event which was restored via Sec72 Gurgaon(HR) through Gurgaon(PG) by 18:00 hrs. 1) 400/220 kV 500 MVA ICT 1 at Sohna Road (GPTL) 2) 400/220 kV 500 MVA I | grid_india_gd/grid_events/2026-08-01
G00438 | 2026-08 | 31 | GD-1 | Gujarat | GJ | Western | 2026-08-08T20:31 | 2026-08-08T22:28 | 1.95 | 25 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 25 MW occurred at Kotda Madh due to loss of evacuation path. | 7 GD-1 Gujarat 08-08-2026 20:31 08-08-2026 22:28 01:57 25 0 0.04% 0.00% 65 663 55862 Complete outage of 220 kV Kotda Madh S/S: At 20:31 hrs /08-08-2026 , Bph-E fault occurred on 220kV Bhuj Kotda Madh line. Associated Bay 231 breaker failure at Bhuj end led to LBB protection operation and tripping of 220kV-Bhuj Bus-6 with elements connected to it. Generation loss of 25 MW occurred at Kotda Madh due to loss of evacuation path. Tripping of following Elements: 1 220KV Kotda Madh (Netra) - Bhuj 2 220KV Bhuj Bus-6 3 220kV Bus coupler (Bay 224) at Bhuj PS 4 220kV Bus Sectionalizer (Bay 229) at Bhuj PS 5 500MVA 400/220kV ICT#8 at Bhuj PS 6 220KV Kotda Madh – Bus-1 7 220KV Kotda Madh – Bus-2 8 220KV Kotda Madh – ICT-1 9 220KV Kotda Madh – ICT-2 | grid_india_gd/grid_events/2026-08-01
G00439 | 2026-08 | 9 | GD-1 | Haryana and Chandigarh |  |  | 2026-08-10T10:34 | 2026-08-10T12:39 | 2.08 | 0 | 175 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GD-1 Haryana and Chandigarh 10-08-2026 10:34 10-08-2026 12:39 02:05 0 175 0.00% 0.23% 74621 74994 i)400/220kV Panchkula(PG) has double main and transfer bus scheme at 220kV level. 220/66kV Rawli(HV) has double main bus scheme at 220kV level and is connected with 400/220kV Panchkula(PG) through 220 | 9 GD-1 Haryana and Chandigarh 10-08-2026 10:34 10-08-2026 12:39 02:05 0 175 0.00% 0.23% 74621 74994 i)400/220kV Panchkula(PG) has double main and transfer bus scheme at 220kV level. 220/66kV Rawli(HV) has double main bus scheme at 220kV level and is connected with 400/220kV Panchkula(PG) through 220 KV Rawli(HV)-Panchkula(PG) (HVPNL) Ckt-1 & Ckt-2. ii)During antecedent condition, 400/220 kV 315 MVA ICT 1&2 at Panchkula(PG) were carrying ~130MW each and 400/220 kV 500 MVA ICT 3 at Panchkula(PG) was carrying ~222MW. 220 KV Rawli(HV)-Panchkula(PG) (HVPNL) Ckt-1 was under planned shutdown. iii)As reported, at 10:34 hrs, bus bar protection of 220kV Bus-1 operated (reason for operation of bus bar protection is yet to be shared). iv)Operation of bus bar protection resulted in tripping of all elements connected with the bus-1. v)As 220 kV Rawli(HV)-Panchkula(PG) (HVPNL) Ckt-1 was already under planned shutdown, tripping of 220 KV Rawli(HV)-Panchkula(P G) (HVPNL) Ckt-2 led to complete blackout of 220/66kV Rawli(HV) substation. vi)As per PMU at Panchkula(PG), R-Y phase to phase fault was observed; however, fault details are yet to be shared by POWERGRID. vii)As per SCADA, change in demand of approx 165 MW was observed in Haryana control area and approx 10 MW in Chandigarh control area. 1) 220KV Bus 1 at Panchkula(PG) 2) 400/220 kV 315 MVA ICT 1 at Panchkula(PG) 3) 220 KV Panchkula-Chandigarh Sec-47 (PG) Ckt-2 4) 220 KV Panchkula(PG)-Pinjore (HV) (HVPNL) Ckt-1 5) 220 KV Panchkula(PG)-Pa | grid_india_gd/grid_events/2026-08-01
G00440 | 2026-08 | 32 | GD-1 | Gujarat | GJ | Western | 2026-08-10T13:26 | 2026-08-10T20:57 | 7.52 | 105 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss 105 MW occurred at 220 kV Sidhpur RE station due to loss of evacuation path. | 8 GD-1 Gujarat 10-08-2026 13:26 10-08-2026 20:57 07:31 105 0 0.14% 0.00% 7 4668 64286 Complete outage of 220 kV Sidhpur(Torrent) S/S: At 13:26 hrs/ 10-08-26, 220kV Sidhpur Jamkhambaliya S/C tripped due to Y phase-E fault. Generation loss 105 MW occurred at 220 kV Sidhpur RE station due to loss of evacuation path. Tripping of following Elements: 1 220kV Sidhpur Jamkhambaliya S/C 2 220/33kV ICT-1,2&3 at Sidhpur Elements Tripped Details of Grid Events during the Month of August 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of August 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief det | grid_india_gd/grid_events/2026-08-01
G00441 | 2026-08 | 33 | GI-1 | Madhya Pradesh | MP | Western | 2026-08-11T05:27 | 2026-08-11T06:53 | 1.43 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GI-1 Madhya Pradesh 11-08-2026 05:27 11-08-2026 06:53 01:26 0 0 0.00% 0.00% 79954 68657 Complete outage of 220 kV Mehgaon) S/S: At 05:27 Hrs/11-08-2026, 220 kV Mehgaon Auraiya & 220 kV Mehgaon Morena line (tripped at Morena end only) tripped on R-E fault. At the same time, 220/132kV 200 MVA ICT-1 | 9 GI-1 Madhya Pradesh 11-08-2026 05:27 11-08-2026 06:53 01:26 0 0 0.00% 0.00% 79954 68657 Complete outage of 220 kV Mehgaon) S/S: At 05:27 Hrs/11-08-2026, 220 kV Mehgaon Auraiya & 220 kV Mehgaon Morena line (tripped at Morena end only) tripped on R-E fault. At the same time, 220/132kV 200 MVA ICT-1 & 220/132kV 160 MVA ICT-2 tripped on differential protection operation. With these trippings, 220kV Mehgaon substation went dark. Tripping of following Elements: 1 220 kV Mehgaon- Morena 2 220 kV Mehgaon- Auraiya 4 220/132 kV 200 MVA ICT 1 5 220/132 kV 200 MVA ICT 2 | grid_india_gd/grid_events/2026-08-01
G00442 | 2026-08 | 47 | GD-1 | Jharkhand | JH | Eastern | 2026-08-11T16:25 | 2026-08-11T17:11 | 0.77 | 0 | 60 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 Jharkhand 11-08-2026 16:25 11-08-2026 17:11 00:46 0 60 0.00% 0.20% 30471 29423 At 16:25 Hrs on 11/08/2026, R-Earth fault was occurred in 132kV line from Chatra S/s which was not cleared from 132kV line protection and same fault was sensed by Latehar and Daltonganj end in Z-3 protection. After | 1 GD-1 Jharkhand 11-08-2026 16:25 11-08-2026 17:11 00:46 0 60 0.00% 0.20% 30471 29423 At 16:25 Hrs on 11/08/2026, R-Earth fault was occurred in 132kV line from Chatra S/s which was not cleared from 132kV line protection and same fault was sensed by Latehar and Daltonganj end in Z-3 protection. After 800 msec both line got tripped in Z-3 protection from remote end, resulting in 220kV Chatra S/s became dead. Total load loss of 60 MW was reported at Chatra S/s. 220KV-DALTONGANJ-CHATRA-1 220 kV Latehar–Chatra | grid_india_gd/grid_events/2026-08-01
G00443 | 2026-08 | 10 | GI-1 | Punjab | PB | Northern | 2026-08-12T10:11 | 2026-08-12T12:18 | 2.12 | 0 | 132 | FALSE | FALSE | FALSE | FALSE | FALSE | Further, 220 kV Ghulal (PS) is connected to Ropar Thermal Plant through a 220 kV single circuit. | 10 GI-1 Punjab 12-08-2026 10:11 12-08-2026 12:18 02:07 0 132 0.00% 0.18% 68 530 74183 i)400/220kV Ludhiana(PG) has a double main and transfer bus scheme at the 220kV level. 220/66kV Sahnewal(PS) has a double main bus scheme. Sahnewal(PS) is connected to 400/220kV Ludhiana(PG), 220/66kV Doraha(PS), and 220kV Ghulal(PS) through 220kV Ludhiana(PG)–Sahnewal(PS) (PSTCL) Ckt-1 and Ckt-2, 220kV Sahnewal–Doraha(PS) Ckt-1 and Ckt-2, and 220kV Sahnewal–Ghulal(PS) Ckt, respectively. Further, 220 kV Ghulal (PS) is connected to Ropar Thermal Plant through a 220 kV single circuit. ii)During the antecedent condition, 220kV Ludhiana(PG)–Sahnewal(PS)(PSTCL) Ckt-1 and Ckt-2 were supplying ~340 MW to 220/66kV Sahnewal(PS), while 220kV Ludhiana(PG)–Doraha(PS)(PSTCL) Ckt-1 was supplying ~110 MW to 220/66kV Doraha(PS) (as per SCADA). iii)As reported, at 10:11 hrs, 220kV Ludhiana(PG)–Sahnewal(PS)(PSTCL) Ckt-2 tripped due to B-N phase to earth fault with fault current of ~9.5kA and fault distance of ~16.19KM from Ludhiana(PG) end, and fault current of ~10.86kA and fault distance of ~6.13KM from Sahnewal(PS); fault was sense d in zone-2 from Ludhiana(PG) and zone-1 from Sahnewal(PS). At the same time, 220kV Ludhiana(PG)–Sahnewal(PS)(PSTCL) Ckt-1 tripped from Sahnewal end only due to RYB three phase fault (exact location of fault and details of the protection operated are yet to be shared). iv)As per the PMU at Ludhiana(PG), a B-N phase-to-earth fault was observed, with a fault-clearing time of 560 ms | grid_india_gd/grid_events/2026-08-01
G00444 | 2026-08 | 11 | GD-1 | Punjab | PB | Northern | 2026-08-12T10:17 | 2026-08-12T12:18 | 2.02 | 0 | 402 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GD-1 Punjab 12-08-2026 10:17 12-08-2026 12:18 02:01 0 402 0.00% 0.54% 68 794 74494 i)400/220kV Ludhiana(PG) has a double main and transfer bus scheme at the 220 kV level. 220/66 kV Doraha(PS) has a double main bus scheme. Doraha(PS) is connected to 220/66 kV Sahnewal(PS) through 220 kV Sahnewal–D | 11 GD-1 Punjab 12-08-2026 10:17 12-08-2026 12:18 02:01 0 402 0.00% 0.54% 68 794 74494 i)400/220kV Ludhiana(PG) has a double main and transfer bus scheme at the 220 kV level. 220/66 kV Doraha(PS) has a double main bus scheme. Doraha(PS) is connected to 220/66 kV Sahnewal(PS) through 220 kV Sahnewal–Doraha(PS) Ckt-1 and Ckt-2 and to 400/220 kV Ludhiana(PG) through 220 kV Ludhiana(PG)–Doraha(PS) (PSTCL) Ckt- 1. Further, 220/66 kV Sahnewal(PS) is connected to 400/220 kV Ludhiana(PG) through 220 kV Ludhiana(PG)–Sahnewal(PS) (PSTCL) Ckt-1 and Ckt-2. 220 kV Ghulal(PS) has a double main bus scheme and is connected to Ropar Thermal and 22 0 kV Sahnewal(PS). ii)Under the antecedent condition, 220kV Ludhiana(PG)–Sahnewal(PS) (PSTCL) Ckt-1 and Ckt-2 had tripped due to the event at 10:11 hrs. 220 kV Ludhiana(PG)–Doraha(PS) (PSTCL) Ckt-1 was carrying ~338 MW of power (as per SCADA). Both circuits at 220 kV Ghulal (i.e., to Ropar Thermal and Sahnewa l(PS)) were connected to separate buses, and the bus coupler was closed. iii)As reported, at 10:17 hrs, 220kV Ludhiana(PG)–Doraha(PS) (PSTCL) Ckt-1 tripped due to an R-N phase-to-earth fault, with a fault current of 20.16 kA and fault distance of 5.23 km from the Ludhiana(PG) end. iv)As a result, the 220 kV Ghulal(PS)–Sahnewal(PS) circuit became the only remaining power source for Sahnewal(PS) and Doraha(PS). This led to overloading of the bus coupler at 220 kV Ghulal(PS), causing it to trip. Consequently, a blackout occurred at 220 kV Sahnewal( | grid_india_gd/grid_events/2026-08-01
G00445 | 2026-08 | 48 | GD-1 | Sikkim | SK | Eastern | 2026-08-13T07:28 | 2026-08-13T09:02 | 1.57 | 105 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Total generation loss of 105 MW reported at Dikchu HEP S/s. | 2 GD-1 Sikkim 13-08-2026 07:28 13-08-2026 09:02 01:34 105 0 0.30% 0.00% 35 233 27468 Prior to the disturbance Dikchu HEP generation was around 105 MW evacuating through 400kV Rangpo-Dikchu S/C line. At 07:28 Hrs on 13/08/2026, transient B- Earth fault was occurred in line and line got tripped from Dikchu end only (A/r successful from Rangpo end), resulting in 400kV Dikchu HEP became dead. Total generation loss of 105 MW reported at Dikchu HEP S/s. 400 kV Dikchu -Rangpo -1 Dikchu HEP Unit-1 (48 MW) Dikchu HEP Unit-2 (48 MW) Elements Tripped Details of Grid Events during the Month of August 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD I Arunachal Pradesh 04-08-2026 09:31 04-08-2026 12:45 03:14 0 20 0.00% 0.73% 3427 2732 The 132 kV Along and 132 kV Basar areas of the Arunachal Pradesh power system were connected to the rest of the NER grid through the 132 kV Along–Pasighat and 132 kV Basar–Baporijo transmission lines. The 132 kV Dapo | grid_india_gd/grid_events/2026-08-01
G00446 | 2026-08 | 12 | GI-2 | Haryana | HR | Northern | 2026-08-15T07:06 | 2026-08-15T16:26 | 9.33 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 12 GI-2 Haryana 15-08-2026 07:06 15-08-2026 16:26 09:20 0 0 0.00% 0.00% 595 83 70146 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2000 MW of power from Champa to Kurukshetra (~500 MW on each pole) (as per SCADA). ii)As reported, at 07:06 hrs, T | 12 GI-2 Haryana 15-08-2026 07:06 15-08-2026 16:26 09:20 0 0 0.00% 0.00% 595 83 70146 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2000 MW of power from Champa to Kurukshetra (~500 MW on each pole) (as per SCADA). ii)As reported, at 07:06 hrs, Teed Differential Protection of the R-phase operated due to the failure of the R-phase LA in the Pole-1 PLC yard at Kurukshetra(PG). The failure of LA resulted in a transient system disturbance, leading to commu tation failure and the subsequent blocking of Pole-1 and Pole-2 at Kurukshetra(PG). iii)As reported, Pole-1 87TT-1 & 87TT-2 (TEED-1&2 Protection) recorded high differential currents (IA Diff ≈ 12.5 pu), along with significant transient current and voltage oscillations during the disturbance. Analysis indicates that th e 87TT operation was consequential to the severe system transie nt initiated by the LA failure. Disturbance record analysis indicates that HV-side fault current of approxi mately 46.07 kA in R-phase. iv)As reported, Pole-2 received an External Block due to operation of 87TT-1 Teed Differential Protection in R-Phase. During the event, 87TT-1 operated, whereas 87TT-2 did not operate. A significant difference in the current inputs use d by 87TT-1 were found at a moment (i.e. Main CT: 2100 A, Tie CT: 400 A & Converter CT (YY & YA): 1200 A). The current imbalance resulted in the operation of Teed Differentia l Protection (87TT-1) in R-Phase. v)As per the PMU at Kuru | grid_india_gd/grid_events/2026-08-01
G00447 | 2026-08 | 13 | GD-1 | Punjab | PB | Northern | 2026-08-16T00:04 | 2026-08-16T01:33 | 1.48 | 0 | 458 | FALSE | FALSE | FALSE | FALSE | FALSE | Amritsar(PS)-Khasa(PS) (PSTCL) Ckt-1 2) 220 KV Amritsar(PG)-Khasa(PS) (PSTCL) Ckt-1 3) 220 KV Amritsar(PG)-Khasa(PS) (PSTCL) Ckt-2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of August 2026 in Northern Region Elements Tripped Sl | 13 GD-1 Punjab 16-08-2026 00:04 16-08-2026 01:33 01:29 0 458 0.00% 0.59% 56 811 78101 i)220/66kV Khassa(PS) has a single bus scheme at the 220kV level. 220/66kV Khassa(PS) is connected with 400/220kV Amritsar(PG) through 220 KV Amritsar(PG)-Khasa(PS) (PSTCL) Ckt-1 and Ckt-2. Further, 220kV CL Amristsar(PS) and 220kV Chogawan(PS) are connected with 220/66kV Khassa(PS) through 220 KV C.L. Amritsar(PS)-Khasa(PS) (PSTCL) Ckt and 220 KV Chogawan(PS)- Khasa(PS) (PSTCL) Ckt, respectively. ii)During the antecedent condition, as reported, 220kV C.L. Amritsar(PS)–Fatehgarh Churia(PS) Ckt and 220kV Majitha(PS) – Fatehgarh Churia(PS) Ckt were already open. As a result, 220 KV Amritsar(PG)-Khasa(PS) (PSTCL) Ckt-1 and Ckt-2 were the only power sources to the 220kV Khassa(PS), 220kV Civil Line Amritsar(PS), 220kV Chogawan(PS), and 220kV Majitha(PS) substations and were carrying ~354MW of power to 220/66kV Khassa(PS) station (as per SCADA). iii)As reported, at 00:04 hrs, the B-phase CT of 220 KV C.L. Amritsar(PS)-Khasa(PS) (PSTCL) Ckt-1 at Khassa(PS) got damaged, resulting in the tripping of this line on a B-N phase-to-earth fa ult with a fault current of 13.26kA at the Khassa(PS) end. iv)As reported, at the same time, 220 KV Amritsar(PG)-Khasa(PS) (PSTCL) Ckt-1 tripped from the Khasa(PS) end due to an R-B phase-to-phase fault in zone-4, with a fault current of 5.9kA & Ib=3.4kA and a fault distance of 235.8 meters from the Khassa(P S) end. At the same time, 220 KV Amritsar(PG)-Khasa(PS) (PST | grid_india_gd/grid_events/2026-08-01
G00448 | 2026-08 | 14 | GD-1 | Rajasthan | RJ | Northern | 2026-08-17T08:44 | 2026-08-17T10:00 | 1.27 | 303 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 303 MW at Azure43(IP) was observed. | 14 GD-1 Rajasthan 17-08-2026 08:44 17-08-2026 10:00 01:16 303 0 0.47% 0.00 % 64775 68675 i)Azure43PSS(IP) and Azure43RSS(IP) has one and half breaker scheme. Generation of 400kV Azure43PSS(IP) and Azure43RSS(IP) evacuates through 400 KV Bikaner(PG)- AzurePSS43 SL_BKN_PG(Azure) (Azure) Ckt. ii)During antecedent conditions, 400kV Azure43PSS(IP) and 400kV Azure43RSS(IP) were generating approx 303 MW (as per SCADA). iii)As reported, at 08:44 hrs, 400 KV Bikaner(PG)-AzurePSS43 SL_BKN_PG(Azure) (Azure) Ckt tripped (exact reason and nature of protection operated is yet to be shared). This led to complete blackout of 400kV Azure43PSS(IP) and Azure43RSS(IP) stations. iv)At the same time, 400/33 kV 150 MVA ICT 1 at AzurePSS43 SL_BKN_PG(Azure) also tripped (exact reason and nature of protection operated is yet to be shared). v)As per PMU at Bikaner(IP), Y-N phase to earth fault converted to Y-B-N double phase to earth fault was observed with fault clearing time of 320 msec. vi)As per SCADA, generation loss of approx 303 MW at Azure43(IP) was observed. 1) 400 KV BIKANER(PG)-AZUREPSS43 SL_BKN_PG(AZURE) (AZURE) CKT-1 2) 400/33 kV 150 MVA ICT 1 at AzurePSS43 SL_BKN_PG(Azure) | grid_india_gd/grid_events/2026-08-01
G00449 | 2026-08 | 34 | GD-1 | Madhya Pradesh | MP | Western | 2026-08-19T11:04 | 2026-08-19T12:43 | 1.65 | 76 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 76MW occurred. | 10 GD-1 Madhya Pradesh 19-08-2026 11:04 19-08-2026 12:43 01:39 76 0 0.12% 0.00% 65663 55862 Complete outage of 220 kV Shajapur Unit-8 S/S: At 11:04 Hrs, 220 kV Shajapur Unit-8 - Pachora line tripped on Y-E fault. Due to the loss of evacuation path, 220 kV Shajapur Unit-8 Solar Power Plant become dark. Generation loss of 76MW occurred. Tripping of following Elements: 1 220 kV Shajapur Unit-8 -Pachora 2 220/33 kV Shajapur Unit-8 ICT 1 3 220/33 kV Shajapur Unit-8 ICT 2 4 220kV Shajapur Unit-8 Bus-1 5 220kV Shajapur Unit-8 Bus-2 | grid_india_gd/grid_events/2026-08-01
G00450 | 2026-08 | 15 | GI-1 | Uttar Pradesh | UP | Northern | 2026-08-19T12:16 | 2026-08-19T13:15 | 0.98 | 267 | 467 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, a change in demand of ~467 MW was observed in the UP control area, and a generation loss of ~267 MW occurred at Harduaganj(UP). | 15 GI-1 Uttar Pradesh 19-08-2026 12:16 19-08-2026 13:15 00:59 267 467 0.36% 0.62% 74701 74784 i)220/132kV Harduaganj(UP) substation has a double main and transfer bus scheme at 220kV level and a single main and transfer bus arrangement at 132kV level. Three generating units, comprising 1 × 110 MW and 2 × 250 MW units, are connected to the 220kV bus at Harduaganj(UP). ii)During the antecedent condition, Unit-7 and Unit-8 were in service, with the total generation at Harduaganj(UP) ~267 MW (as per SCADA). As reported, 220kV Harduaganj–Khurja(UP) Ckt-1, 220 kV Harduaganj–Atrauli(UP) Ckt, and 400/220kV, 315 MVA ICT-1 were connected to Bus-1. 220kV Harduaganj–Khair(UP) Ckt-2, 220kV Harduaganj–Boner(UP) Ckt, and 400/220kV, 315 MVA ICT-2 were connected to Bus-2. iii)As reported, at 12:16 hrs, the B-phase jumper of 220 kV Harduaganj-Khair Ckt-2 snapped at the 220kV Harduaganj(UP) end and touched the Y-phase jumper at the first tower of the transmission line near the boundary wall of the switchyard. As per DR, a B-N phase-to-earth fault converted to a B-Y-N double- phase-to-earth fault, with fault currents of Ib = 33.1 kA & Iy = 34.8 kA; the fault was sensed in Zone-1 from Harduaganj(UP) wit h a fault-clearing time of ~200 msec. iv)As reported, Busbar & LBB protection is not operational at Harduaganj(UP). Due to this, delayed fault clearance led to the operation of Z-4 protection in multiple lines at Harduaganj(UP) and subsequent tripping of 220kV Harduaganj-Khurja(UP) Ckt-1, 220kV Ha | grid_india_gd/grid_events/2026-08-01
G00451 | 2026-08 | 46 | GI-2 | Andhra Pradesh | AP | Southern | 2026-08-19T12:38 | 2026-08-26T14:32 | 169.9 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 10 GI-2 ANDHRA PRADESH 19-08-2026 12:38 26-08-2026 14:32 169:54 0 0 0.00% 0.00% 57323 68025 Tripping of 765kV Bus-2 of Srikakulam of PGCIL-SR1 As per the reports submitted, the triggering incident was an R-G fault on 765 kV Bus-2 at Srikakulam, suspected to have been caused by a GIS failure. The fault resulted in the operation of the 765 kV Bus-2 busbar protection (BBP), leading to the tripping of all main breakers connected to 765 kV Bus-2 at Srikakulam Substation this led to the tripping of 765kV Bus-2 of Srikakulam of PGCIL-SR1 SRIKAKULAM - 765KV - Bus 2 Details of Grid Events during the Month of August 2026 in Southern Region Elements Tripped SlNo. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-08-01
G00452 | 2026-08 | 16 | GD-1 | Uttarakhand | UK | Northern | 2026-08-19T21:02 | 2026-08-19T22:52 | 1.83 | 0 | 152 | FALSE | FALSE | FALSE | FALSE | FALSE | 16 GD-1 Uttarakhand 19-08-2026 21:02 19-08-2026 22:52 01:50 0 152 0.00% 0 .18% 60586 82565 i)220/132kV SIDCUL(UK) S/s has double main and transfer bus scheme at 220kV level. ii)As reported, under antecedent system conditions, the 220 kV SIDCUL-Pirankaliyar circuit was open; as a result, 220 kV SIDCU | 16 GD-1 Uttarakhand 19-08-2026 21:02 19-08-2026 22:52 01:50 0 152 0.00% 0 .18% 60586 82565 i)220/132kV SIDCUL(UK) S/s has double main and transfer bus scheme at 220kV level. ii)As reported, under antecedent system conditions, the 220 kV SIDCUL-Pirankaliyar circuit was open; as a result, 220 kV SIDCUL-Rishikesh Ckt was the only power source to the 220/132kV SIDCUL. iii)As reported, at 21:02 hrs, 220 kV SIDCUL-Rishikesh (PTCUL) Ckt tripped due to R-N phase to earth fault (exact fault location, fault current and nature of protection operated are yet to be shared). iv)This led to complete blackout of 220/132kV SIDCUL(UK) station. v)As per PMU at Rishikesh(UK), R-N Phase to earth fault was observed with fault clearance time of ~400 msec. vi)As per SCADA, change in demand of approx 152 MW was observed in UƩarakhand control area. 1) 220 kV SIDCUL-Rishikesh (PTCUL) Ckt | grid_india_gd/grid_events/2026-08-01
G00453 | 2026-08 | 17 | GD-1 | Rajasthan | RJ | Northern | 2026-08-20T14:17 | 2026-08-20T14:54 | 0.62 | 130 | 235 | FALSE | FALSE | FALSE | FALSE | FALSE | ix)As per SCADA, approx 235 MW load loss in Rajasthan control area was observed; as reported, ~130 MW generation loss occurred at VSLP generation station. | 17 GD-1 Rajasthan 20-08-2026 14:17 20-08-2026 14:54 00:37 130 235 0.18% 0. 30% 72444 78632 i)220/132kV Bikaner(RS) has double main and transfer bus scheme at 220kV level, and double main bus scheme at 132kV level. 220kV VSLP Generating station is connected to 220/132kV Bikaner(RS) through 220 kV VSLP–Bikaner(RS) single circuit. ii)During antecedent condition, VSLP was generating ~130 MW. iii)As reported, at 14:17 hrs, B-phase jumper of 220kV Barsingsar-Bikaner(RS) Ckt snapped and B-N phase-to-earth fault occurred (fault details and nature of protection operated are yet to be shared). iv)At the same time, zone-4 protection operated in 220 kV Bikaner–Sutargarh(RS) Ckt, 220 kV Bikaner–Bikaner Interconnector-1&2, and 220 kV VSLP–Bikaner(RS) Ckt, resulting in tripping of these lines (exact reason for operation of z-4 p rotection is yet to be shared). v)At the same time, 220kV Bikaner-Badnu(RS) Ckt tripped from Badnu(RS) end due to B-N fault sensed in zone-2 from Badnu(RS) with a fault distance of 66.3 km. vi)This led to complete blackout of 220/132kV Bikaner(RS) station. vii)Tripping of 220 kV VSLP–Bikaner(RS) Ckt resulted in loss of evacuation path for VSLP generating station, and the unit of VSLP tripped. viii)As per PMU at Bhadla(PG), B-N phase-to-earth fault was observed with fault clearing time of 80 msec each. ix)As per SCADA, approx 235 MW load loss in Rajasthan control area was observed; as reported, ~130 MW generation loss occurred at VSLP generation station. 1) 220 kV Bi | grid_india_gd/grid_events/2026-08-01
G00454 | 2026-08 | 18 | GI-2 | Uttar Pradesh | UP | Northern | 2026-08-21T02:34 | 2026-08-21T04:32 | 1.97 | 266 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GI-2 Uttar Pradesh 21-08-2026 02:34 21-08-2026 04:32 01:58 266 0 0.47% 0.00% 56834 78456 i)400kV Singrauli_TPS substation has four-bus scheme at 400kV level. Bus-1 & Bus-3 and Bus-2 & Bus-4 are interconnected with bus sectionalizer; Bus-1 & Bus-2 and Bus-3 & Bus-4 are interconnected with bus coup | 18 GI-2 Uttar Pradesh 21-08-2026 02:34 21-08-2026 04:32 01:58 266 0 0.47% 0.00% 56834 78456 i)400kV Singrauli_TPS substation has four-bus scheme at 400kV level. Bus-1 & Bus-3 and Bus-2 & Bus-4 are interconnected with bus sectionalizer; Bus-1 & Bus-2 and Bus-3 & Bus-4 are interconnected with bus coupler. ii)During antecedent condition, 200MW Unit-1, 3, 4, 5, 6 & 7 at Singrauli_TPS were running and generating total ~1562 MW (as per SCADA). As reported, 200MW Unit-4, 400kV Singrauli(NT)-Allahabad(PG) (PG) Ckt-1, 400 KV Singrauli(NT)-Anpara(UP) (PG) Ckt-1, 200 MW Singrauli STPS - UNIT 1, & 400/132 kV 100 MVA ICT 1 at Singrauli(NT) were connected with Bus-2. iii)As reported, at 02:34 hrs, while taking Unit-4 of Singrauli TPS under outage due to BTL, the Y-phase pole of the CB of Unit-4 opened with a delay of 1 second compared to the other two poles. Due to this, the LBB of the CB of Unit-4 operated. As a result, Bus-2, along with all the elements connec ted to it, tripped. iv)As per SCADA, change in generation of ~266 MW at Singrauli was observed due to tripping of Unit-1 & Unit-4. v)As per PMU at Singrauli(NTPC), no fault was observed. 1) 200 MW Singrauli STPS - UNIT 4 2) 400KV Bus 2 at Singrauli(NT) 3) 400 KV Singrauli(NT)-Allahabad(PG) (PG) Ckt-1 4) 400 KV Singrauli(NT)-Anpara(UP) (PG) Ckt-1 5) 200 MW Singrauli STPS - UNIT 1 6) 400/132 kV 100 MVA ICT 1 at Singrauli(NT) | grid_india_gd/grid_events/2026-08-01
G00455 | 2026-08 | 19 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-08-21T12:02 | 2026-08-21T13:45 | 1.72 | 0 | 161 | FALSE | FALSE | FALSE | FALSE | FALSE | 19 GI-1 Jammu & Kashmir 21-08-2026 12:02 21-08-2026 13:45 01:43 0 161 0.00% 0.21% 73834 76259 i)220/132kV Ziankote S/s have double main bus scheme at 220kV. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~84 MW | 19 GI-1 Jammu & Kashmir 21-08-2026 12:02 21-08-2026 13:45 01:43 0 161 0.00% 0.21% 73834 76259 i)220/132kV Ziankote S/s have double main bus scheme at 220kV. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~84 MW each) was feeding 132kV load at Ziankote. 220kV Wagoora(PG)-Ziankote(JK) D/C were conne cted at other bus and feeding Alusteng, Drass, Kargil, Khalsti and Leh S/s. iii)As reported, at 12:02 hrs, 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 tripped on B-N phase to earth fault with fault distance of 13.65km and fault current of 5.45kA from Amargarh(INDIGRID) end and fault distance of 9.12km and fault current of 6.12kA from Ziankote(JK) end; fault was sensed in zone-1 from both end. iv)During the same time, 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-2 also tripped on B-N phase to earth fault in zone-2 from Amargarh, with fault distance of 26.54km and fault current of 2.3kA from Amargarh(INDIGRID) end (as per EL). v)Due to tripping of 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 & Ckt-2, supply to 132kV load at Ziankote(JK)failed resulted in load loss. vi)As per PMU at Amargarh, B-N phase to earth fault is observed with fault clearing time of 120ms. vii)As per SCADA, change in demand of approx 161 MW is observed in J&K control area. 1) 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 2) 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-2 | grid_india_gd/grid_events/2026-08-01
G00456 | 2026-08 | 20 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-08-21T17:14 | 2026-08-21T19:37 | 2.38 | 0 | 140 | FALSE | FALSE | FALSE | FALSE | FALSE | 20 GI-1 Jammu & Kashmir 21-08-2026 17:14 21-08-2026 19:37 02:23 0 140 0.00% 0.17% 66383 80122 i)220/132kV Ziankote S/s have double main bus scheme at 220kV. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~70 MW | 20 GI-1 Jammu & Kashmir 21-08-2026 17:14 21-08-2026 19:37 02:23 0 140 0.00% 0.17% 66383 80122 i)220/132kV Ziankote S/s have double main bus scheme at 220kV. ii)During antecedent condition, 220kV Ziankote was operating in bus split mode viz. 220kV Amargarh(INDIGRID) –Ziankote(JK) D/C (carrying ~70 MW each, as reported) was feeding 132kV load at Ziankote. 220kV Wagoora(PG)-Ziankote(JK) D/C were connected at other bus and feeding Alusteng, Drass, Ka rgil, Khalsti and Leh S/s. iii)As reported, at 17:14 hrs, 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 tripped on R-N phase to earth fault with fault current of 2.08kA from Amargarh(INDIGRID) end (location of fault is yet to be shared). iv)As reported, during the same time, 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-2 also tripped (exact reason of tripping and nature of protection operated is yet to be shared). v)Due to tripping of 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 & Ckt-2, supply to 132kV load at Ziankote(JK) resulted in load loss. vi)As per PMU at New Amargarh(INDIGRID), R-N phase to earth fault is observed with fault clearing time of 960ms. vii)As reported, load loss of ~140 MW occurred. 1) 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-1 2) 220 kV Amargarh(INDIGRID)-Ziankote(JK) (JK) Ckt-2 | grid_india_gd/grid_events/2026-08-01
G00457 | 2026-08 | 22 | GI-2 | Rajasthan | RJ | Northern | 2026-08-22T13:10 | 2026-08-22T15:26 | 2.27 | 0 | 130 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 400/220 kV 500 MVA ICT 2 at Sangod GSS (RS) 2) 400 KV Kalisindh-Sangod GSS (RS) Ckt-1 3) 400 KV Sangod GSS (RS) - Bus 2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of August 2026 in Northern Region Elements Tripped Sl No. | 22 GI-2 Rajasthan 22-08-2026 13:10 22-08-2026 15:26 02:16 0 130 0.00% 0.17 % 71380 74542 i)400 kV Sangod (RS) has a one-and-a-half-breaker scheme. ii)Under antecedent conditions, 400 kV Bus-1 at Sangod(RS) was under planned outage since 12:11 hrs. At 12:49 hrs, 400/220 kV, 500 MVA ICT-1 at Sangod(RS) and 400 kV Anta–Sangod GSS (RS) Ckt-1 tripped due to the operation of the backup impedance relay of ICT-2. The loading of 400 kV Kalisindh–Sangod GSS (RS) Ckt-1 and 400/220 kV, 500 MVA ICT-2 at Sangod GSS (RS) was ~250 MW. iii)As reported, at 13:10 hrs, 400/220 kV, 500 MVA ICT-2 at Sangod(RS) tripped due to the operation of the backup impedance relay. No fault was observed in the DR of ICT-2. iv)As Bus-1 was under shutdown, 400 kV Kalisindh–Sangod GSS (RS) Ckt-1 was connected only to Bus-2 through the tie bay and main bay of 400/220 kV, 500 MVA ICT-2. Therefore, tripping of ICT-2 also resulted in the tripping of t his circuit. v)As per the PMU at Kota(PG) and DR, no fault was observed. vi)As per SCADA, a change in demand of approx 130 MW was observed in the Rajasthan control area. 1) 400/220 kV 500 MVA ICT 2 at Sangod GSS (RS) 2) 400 KV Kalisindh-Sangod GSS (RS) Ckt-1 3) 400 KV Sangod GSS (RS) - Bus 2 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Details of Grid Events during the Month of August 2026 in Northern Region Elements Tripped Sl No. Affected A | grid_india_gd/grid_events/2026-08-01
G00458 | 2026-08 | 21 | GI-2 | Uttar Pradesh | UP | Northern | 2026-08-22T14:40 | 2026-08-22T19:01 | 4.35 | 372 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 372 MW was observed at Bara TPS (UP). | 21 GI-2 Uttar Pradesh 22-08-2026 14:40 22-08-2026 19:01 04:21 372 0 0.50% 0.00% 74071 79862 i)765/400kV Bara TPS(UP) has oner and half breaker scheme at both 765kV and 400kV level. ii)During antecedent condition, 660 MW Unit-1, 2 & 3 at Bara TPS(UP) were in running condition and generating approx 356 MW, 350 MW, 365MW respectively (as per SCADA). iii)As reported, at 14:40 hrs, Y-phase CB of 705 Tie Bay (connected between 765/400kV 1500 MVA ICT-2 & 765/21 KV 825 MVA GT 2) failed. Consequently, the differential protections of ICT-2 and GT-2 operated, resulting in tripping o f both elements. iv)Due to tripping of GT-2, 660 MW Unit-2 at Bara TPS(UP) also tripped. v)As per PMU at Mainpuri(PG), Y-N phase to earth fault was observed with fault clearing time of 80 msec. vi)As per SCADA, generation loss of approx 372 MW was observed at Bara TPS (UP). 1) 765/400kV 1500 MVA ICT-2 at Bara(UP) 2) 765/21 KV 825 MVA GT 2 AT BARA(UP) 3) 660 MW Unit-2 at Bara TPS(UP) | grid_india_gd/grid_events/2026-08-01
G00459 | 2026-08 | 35 | GD-1 | Gujarat | GJ | Western | 2026-08-23T10:58 | 2026-08-23T11:50 | 0.87 | 450 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GD-1 Gujarat 23-08-2026 10:58 23-08-2026 11:50 00:52 450 0 0.55% 0.00% 8 2502 73086 Complete outage of 220kV KIM (Getco) substation S/S: : At 10:58 hrs on 22-08-2026, the R-phase Sillicon Rubber Insulator of 220 kV Main Bus-2 installed near the 220kV Uttran-2 bay bus gantry at 220kV KIM (GETCO) S | 11 GD-1 Gujarat 23-08-2026 10:58 23-08-2026 11:50 00:52 450 0 0.55% 0.00% 8 2502 73086 Complete outage of 220kV KIM (Getco) substation S/S: : At 10:58 hrs on 22-08-2026, the R-phase Sillicon Rubber Insulator of 220 kV Main Bus-2 installed near the 220kV Uttran-2 bay bus gantry at 220kV KIM (GETCO) Substation flashed over, resulting in operation of the Bus Bar Protection and tripping of 220 kV Bus-2 along with all bays connected to it, including the 220kV Bus Coupler at KIM. With Bus-2 lost, the loading on the two remaining Bus-1 source lines – 220kV Kosamba-2 and 220kV TPGL-1 – increased sharply. 220kV TPGL-1 tripped as intended on the Special Protection Scheme (SPS) provided to prevent overloading of the ICTs at the TPGL/Sugen end; however, 220kV Kosamba-2 also tripped from the KIM end because of an incorrect configuration in its SPS logic, which extended the trip command to its own line breaker instead of confining it to the intended TPGL/Pipodra breakers. With both source lines gone, the entire Bus-1 load transferred to the single remaining 220kV Gothan line; the resulting overload caused the 220kV Bus Coupler at Gothan S/s to trip on time-delayed overcurrent protection roughly 2.1 seconds after pick-up, removing the last source and leaving 220kV Bus-1 at KIM completely dead. The event caused a load loss of approximately 450 MW at 220 kV Kim (GETCO) S/S. Tripping of following Elements: 1 220 kV Bus-2, KIM 2 220 kV Bus Coupler, KIM 3 220/66 kV 160 MVA ICT-1 4 220/66 kV 100 | grid_india_gd/grid_events/2026-08-01
G00460 | 2026-08 | 36 | GD-1 | Madhya Pradesh | MP | Western | 2026-08-23T11:49 | 2026-08-23T15:43 | 3.9 | 330 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 330 MW occurred at 220 kV Umariya Agar Unit-5 due to the loss of evacuation path. | 12 GD-1 Madhya Pradesh 23-08-2026 11:49 23-08-2026 15:43 03:54 330 0 0.40% 0.00% 81863 70549 Complete outage of 220 kV Umariya Agar unit-5 S/S: At 11:49 Hrs / 23-08-2026, 220 kV Umariya (Agar Unit-5)-Pachora line tripped on R-Y fault. Generation loss of 330 MW occurred at 220 kV Umariya Agar Unit-5 due to the loss of evacuation path. Tripping of following Elements: 1 220kV Umariya (Agar) Pachora ckt | grid_india_gd/grid_events/2026-08-01
G00461 | 2026-08 | 37 | GD-1 | Madhya Pradesh | MP | Western | 2026-08-23T11:55 | 2026-08-23T19:37 | 7.7 | 92 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, Generation loss of around 92 MW occured. | 13 GD-1 Madhya Pradesh 23-08-2026 11:55 23-08-2026 19:37 07:42 92 0 0.14% 0.00% 65663 55862 Complete outage of 220 kV Shajapur(Burley) unit-6 S/S:At 11:55 hrs, 220kV Shajapur unit-7 (Dehripal) Shajapur unit-6 (Burley) line tripped on B-E fault. As the substation is radially connected, 220kV Shajapur unit-6 (Burley) SS went dark. Due to loss of evacuation path, Generation loss of around 92 MW occured. Tripping of following Elements: 1 220kV Shajapur unit-7 (Dehripal) Shajapur unit-6 (Burley) line | grid_india_gd/grid_events/2026-08-01
G00462 | 2026-08 | 38 | GD-1 | Maharashtra | MH | Western | 2026-08-24T12:05 | 2026-08-24T18:58 | 6.88 | 68 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, generation loss of around 68 MW occurred. | 14 GD-1 Maharashtra 24-08-2026 12:05 24-08-2026 18:58 06:53 68 0 0.08% 0.0 0% 84391 72371 Complete outage of 220 kV Zura S/S: At 12:05 Hrs, While hand tripping 220/33kV Zura ICT-1 (H/T due to flashover occurred on HV side Y phase isolator), 220kV Bhuj- Zura S/C line tripped at Bhuj end only on DT receipt. As the substation is radially connected, 220kV Zura S/S went dark. Due to loss of evacuation path, generation loss of around 68 MW occurred. Tripping of following Elements: 1 220kV Bhuj- Zura S/C line | grid_india_gd/grid_events/2026-08-01
G00463 | 2026-08 | 40 | GD-1 | Madhya Pradesh | MP | Western | 2026-08-25T13:44 | 2026-08-25T17:14 | 3.5 | 72 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | 16 GD-1 Madhya Pradesh 25-08-2026 13:44 25-08-2026 17:14 03:30 72 0 0.09% 0.00% 76242 70054 Complete outage of 220 kV Badi(RUMSL) S/S: At 13:44 hrs / 25-08-2026, B-phase Lightning Arrester (LA) of 33/0.433 kV, 500 kVA Distribution Transformer at 220/33 kV Badi (RUMSL) Solar Plant blasted. | 16 GD-1 Madhya Pradesh 25-08-2026 13:44 25-08-2026 17:14 03:30 72 0 0.09% 0.00% 76242 70054 Complete outage of 220 kV Badi(RUMSL) S/S: At 13:44 hrs / 25-08-2026, B-phase Lightning Arrester (LA) of 33/0.433 kV, 500 kVA Distribution Transformer at 220/33 kV Badi (RUMSL) Solar Plant blasted. Simultaneously, 220 kV Neemuch-Badi-1 S/C, 220/33 kV Badi-ICT-1&2 (110 MVA each) tripped on Earth Fault protection operated (as informed by site). Tripping of following Elements: 1 220 kV Neemuch-Badi-1 S/C 2 220/33 kV Badi-ICT-1 110 MVA 3 220/33 kV Badi-ICT-2 110 MVA | grid_india_gd/grid_events/2026-08-01
G00464 | 2026-08 | 39 | GD-1 | Madhya Pradesh | MP | Western | 2026-08-25T14:58 | 2026-08-25T15:31 | 0.55 | 120 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 15 GD-1 Madhya Pradesh 25-08-2026 14:58 25-08-2026 15:31 00:33 120 0 0.14% 0.00% 84392 72371 Complete outage of 400 kV Kolhapur S/S: At 14:58 hours, a grid disturbance occurred at the 400/220 KV Kolhapur substation in Maharashtra during planned annual maintenance on Main Bus 1. As operations personn | 15 GD-1 Madhya Pradesh 25-08-2026 14:58 25-08-2026 15:31 00:33 120 0 0.14% 0.00% 84392 72371 Complete outage of 400 kV Kolhapur S/S: At 14:58 hours, a grid disturbance occurred at the 400/220 KV Kolhapur substation in Maharashtra during planned annual maintenance on Main Bus 1. As operations personnel were sequentially transferring bays back to Main Bus 2 via the transfer bus, the Y-phase earth switch of the 400/220 KV Inter-Connecting Transformer (ICT) 1 was inadvertently left closed. When the Main Circuit Breaker was subsequently closed onto this active ground, it triggered a Bus 2 fault that instantly tripped all connected 400 KV transmission lines, leaving Kolhapur (MH) Bus 2& S/S completely dead. No load loss occurred. 120 MW load loss occurred at Goa, nil in MH. Tripping of following Elements: 1 400 KV Kolhapur Karad ckt 1 2 400 KV Kolhapur Karad ckt 2 3 400 KV Kolhapur Kolhapur(PG) ckt 1 4 400 KV Kolhapur Kolhapur(PG) ckt 2 5 400 KV Kolhapur Alkud ckt 6 400/220 KV 500 MVA Kolhapur ICT 1 7 400/220 KV 315 MVA Kolhapur ICT 2 8 400/220 KV 500 MVA Kolhapur ICT 3 9 400 KV Kolhapur Bus 1 10 400 KV Kolhapur Bus 2 11 220 KV bus coupler at Amona 12 220 KV Amona Mahalaxmi ckt 13 220 KV Amona Tillari ckt 14 220 KV Amona Bus 1 | grid_india_gd/grid_events/2026-08-01
G00465 | 2026-08 | 41 | GD-1 | Maharashtra | MH | Western | 2026-08-26T17:10 | 2026-08-26T17:10 | 0 | 82 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, generation loss of 82 MW occurred. | 17 GD-1 Maharashtra 26-08-2026 17:10 26-08-2026 17:10 00:00 82 0 0.10% 0.0 0% 84527 70740 Complete outage of 220 kV Zura S/S: At 17:10 Hrs, 220kV Bhuj- Zura S/C line tripped at Bhuj end only on DT receipt. At the same time SVG (connected to bay no. 309) at Jhura also tripped due to under voltage operation. As the substation is radially connected, 220kV Zura S/S went dark. Due to loss of evacuation path, generation loss of 82 MW occurred. Code issued to normalize the line. Tripping of following Elements: 1 220kV Bhuj- Zura S/C line Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 ANDHRA PRADESH 01-08-2026 13:54 01-08-2026 15:04 01:10 0 0 0.00% 0.00% 64725 62534 Complete outage of 220kV Dhone SS of APTRANSCO As per reports submitted, the triggering incident was the B phase CT failure of Bus Coupler which was connected to Bus 2 at 220 kV DHONE substation with comes in the overlap zone of BBP. Upon sensing the fault busbar protection of the buses got triggered and it tripped the two buses of the substation which led to tripping of all elements in the substation leading to the Complete outage of 220kV Dhone SS of APTRANSCO 220KV-DHONE-KAMBALPADU-1, 220KV-DHONE- KRISHNAGIRI-1, 220KV-DHONE-NANSURALLA-1, 220KV- GOOTY-SWS-DHONE-1, 220KV-GOOTY-SWS-DHONE-2, 220KV-SOMAYAJULAPALLI-DHONE-1, 220KV- SOMAYAJULAPALLI-DHONE-2 2 GD - 1 PONDICHERRY 16-08-2026 09:0 | grid_india_gd/grid_events/2026-08-01
G00466 | 2026-08 | 23 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-08-27T20:59 | 2026-08-28T13:18 | 16.32 | 0 | 97 | FALSE | FALSE | FALSE | FALSE | FALSE | 23 GD-1 Jammu & Kashmir 27-08-2026 20:59 28-08-2026 13:18 16:19 0 97 0.00% 0.12% 57668 80892 i)220/132kV Ramban(JK) Substation has a double-main-bus scheme at the 220kV level and is connected to 400/220 kV Kishenpur(PG) and 220/132kV Mirbazar(JK) through 220kV Kishenpur(PG)–Ramban(JK) (JK) Ckt-1 and | 23 GD-1 Jammu & Kashmir 27-08-2026 20:59 28-08-2026 13:18 16:19 0 97 0.00% 0.12% 57668 80892 i)220/132kV Ramban(JK) Substation has a double-main-bus scheme at the 220kV level and is connected to 400/220 kV Kishenpur(PG) and 220/132kV Mirbazar(JK) through 220kV Kishenpur(PG)–Ramban(JK) (JK) Ckt-1 and 220 kV Mirbazar–Ramban(JK) Ckt-1, respectively. ii)Under the antecedent condition, 220 kV Kishenpur(PG)–Ramban(JK) (JK) Ckt-1 was supplying ~70 MW, as per SCADA, from Kishenpur(PG) to 220kV Ramban(JK). As reported, a portion of this power was supplying the local load at Ramban( JK), while the remaining power was being transmitted to 220kV Mirbazar(JK) through 220kV Mirbazar–Ramban(JK) Ckt-1. At the time, Mirbazar(JK) was operat ing in split-bus mode, and the power received from Ramban(JK) w as supplying the 132kV load at Mirbazar(JK). iii)At 20:59 hrs, 220 kV Kishenpur(PG)–Ramban(JK) (JK) Ckt-1 tripped due to a B-N phase-to-earth fault. The fault was located at ~48.94 km from the Kishenpur(PG) end, with a fault current of ~2.58kA. The fault was sensed in Zone-1 at Kishenpur(PG) end. As per the DR data, no auto-reclosure attempt w as initiated. iv)Since 220kV Mirbazar(JK) was operating in split-bus mode, no alternate source was available to maintain the supply to Ramban(JK). Consequently, tripping of 220 kV Kishenpur(PG)–Ramban(JK) (JK) Ckt-1 resulted in the blackout of 220/132kV Ramban(JK) Substation, leading to subsequent load loss. v)As per the PMU at Kishenpur(PG), a B-N phase- | grid_india_gd/grid_events/2026-08-01
G00467 | 2026-08 | 49 | GI-1 | Nagaland | NL | North-Eastern | 2026-08-30T23:55 |  |  | 31 |  | FALSE | FALSE | FALSE | FALSE | FALSE | At 23:55 Hrs of 30-08-2026, Doyang Unit-2 and 3 tripped due to emergency electrical lockout and 132 kV Doyang-Sanis Line tripped leading to generation loss of 48 MW . | 45 GI-1 Nagaland 30-08-2026 23:55 31-08-2026 01:39 1:44:00 48 0 1.35% 0.00% 3563 3314 Doyang HEP, NEEPCO was connected with rest of NER Grid through 132kV Doyang – Mokokchung, 132kV Dimapur-Doyang D/C and 132kV Doyang-Sanis lines. (Doyang Unit-1 was under forced outage since 17:51 Hrs of 22-08-2026). At 23:55 Hrs of 30-08-2026, Doyang Unit-2 and 3 tripped due to emergency electrical lockout and 132 kV Doyang-Sanis Line tripped leading to generation loss of 48 MW . The unit 2 and Unit 3 got synchronised at 01:39 Hrs and 1:59 Hrs of 31-08-2026 respectively. Doyang Unit-2, Doyang unit 3, 132 kV Doyang-Sanis Line | grid_india_gd/grid_events/2026-08-01
G00468 | 2026-08 | 50 | GI-1 | Meghalaya | ML | North-Eastern | 2026-08-31T11:51 | 2026-08-31T12:30 | 0.65 | 125 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 46 GI-1 Meghalaya 31-08-2026 11:51 31-08-2026 12:30 00:39 125 0 3.49% 0.00% 3582 2834 Leshka is radially connected through 132 kV Mynkre – Leshka 1 & 2 lines only. At 11:51 Hrs of 31-08-2026 all the units tripping due to the fault in the 132 kV interconnecting lines from the powerhouse to switchyard | 46 GI-1 Meghalaya 31-08-2026 11:51 31-08-2026 12:30 00:39 125 0 3.49% 0.00% 3582 2834 Leshka is radially connected through 132 kV Mynkre – Leshka 1 & 2 lines only. At 11:51 Hrs of 31-08-2026 all the units tripping due to the fault in the 132 kV interconnecting lines from the powerhouse to switchyard. The fault in the lines got cleared by the tripping of units. The units got synchronsied at 12:30 Hrs, 13:43 Hrs and 15:50 Hrs of 31-08-2026 respectively. Leshka Unit 1, Leshka Unit 2, Leshka Unit 3 | grid_india_gd/grid_events/2026-08-01
G00469 | 2026-08 | 24 | GI-2 | Himachal Pradesh | HP | Northern | 2026-08-31T11:56 | 2026-08-31T12:12 | 0.27 | 703 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, a generation loss of ~703 MW [~273 MW at Nathpa Jhakri, ~74 MW at Rampur HEP , ~286 MW at Karcham Wangtoo HEP , ~37 MW at Sawra Kuddu HEP , and ~33 MW at Naitwar Mori HEP] was observed. | 24 GI-2 Himachal Pradesh 31-08-2026 11:56 31-08-2026 12:12 00:16 703 0 0.98% 0.00% 71832 78150 i)As per the logic of SPS (Case-1) at the Jhakri, Rampur, and Karcham complex, if the load on any of the lines at Jhakri, Rampur, or Gumma towards Nalagarh or Panchkula exceeds 900 MW, one unit each of Karcham Wangtoo HEP, Jhakri HEP, Rampur HEP, Sawra Kuddu (Gumma) HEP, and Naitwar Mori HEP shall trip. ii)During the antecedent condition, all units of NJPC HPS were running with a total generation of ~1640 MW (Unit-3 generation was ~273 MW), all units of Rampur HPS were running with a total generation of ~433 MW (Unit-5 generation w as ~74 MW), all units of Karcham Wangtoo HPS were running with a total generation of ~1137 MW (Unit-2 generation was ~286 MW), only Unit-1 at Sawra Kuddu was running and generating ~37 MW, and the total generation at Naitwar Mori HPS was ~65 MW (Unit-1 was generating ~33 MW). 400kV Rampur HEP(SJ)-Nallagarh(PG)(PG) Ckt-1 & Ckt-2 were carrying ~780 MW each. iii)As reported, at 11:56 hrs, the 400kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-1 tripped due to a Y-B phase-to-phase fault, with fault currents of Iy = 17 kA and Ib = 18 kA from the Nallagarh(PG) end, and Iy = 4.5 kA and Ib = 4.5 kA from the Rampur(SJVN) end. The fault was sensed in Zone-1 from the Nallagarh(PG) end and in Zone-2 from the Rampur(SJVN) end. iv)Due to the tripping of this circuit, the loading of the 400 kV Rampur HEP(SJ)-Nallagarh(PG) (PG) Ckt-2 exceeded 900 MW, and SPS (Case-1) operated a | grid_india_gd/grid_events/2026-08-01
G00470 | 2026-08 | 51 | GI-1 | Tripura | TR | North-Eastern | 2026-08-31T14:52 |  |  | 31 |  | FALSE | FALSE | FALSE | FALSE | FALSE | 47 GI-1 Tripura 31-08-2026 14:52 31-08-2026 16:05 1:13:00 0 164 0.00% 5.30% 3593 3095 Surajmaninagar (TE) is connected to the rest of the North Eastern Region (NER) grid through the lines as below: 132 kV Surajmaninagar–Palatana line 132 kV Surajmaninagar (ST)–Surajmaninagar (TE) line 132 kV Surajma | 47 GI-1 Tripura 31-08-2026 14:52 31-08-2026 16:05 1:13:00 0 164 0.00% 5.30% 3593 3095 Surajmaninagar (TE) is connected to the rest of the North Eastern Region (NER) grid through the lines as below: 132 kV Surajmaninagar–Palatana line 132 kV Surajmaninagar (ST)–Surajmaninagar (TE) line 132 kV Surajmaninagar–Buddhajannagar line 132 kV Agartala–Surajmaninagar D/C line In addition, Surajmaninagar (TE) is interconnected with the Bangladesh power system through the 132 kV Surajmaninagar–Comilla D/C transmission line. At 14:52 hrs, all the transmission lines emanating from 132 kV Surajmaninagar (S.M. Nagar) Bus-I and Bus-II, except the 132 kV Surajmaninagar–Buddhajannagar line, tripped along with the bus-coupler breaker. Hence, Bus II was in idle charged condition. System normalised after closing of the 132 kV 132 kV Agartala–Surajmaninagar D/C lines at 16:05 Hrs of 31-08-2026. 132 kV Surajmaninagar–Palatana, 132 kV Agartala–Surajmaninagar -1, 132 kV Agartala–Surajmaninagar - 2, 132 kV Surajmaninagar–Comilla-1, 132 kV Surajmaninagar–Comilla-2, 132 kV Bus Coupler | grid_india_gd/grid_events/2026-08-01
G00471 | 2026-09 | 15 | GD-1 | Gujarat | GJ | Western | 2026-09-01T19:59 | 2026-09-01T23:32 | 3.55 | 18 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 18 MW occurred at Manza Wind Power Plant due to loss of single evacuation path. | 1 GD-1 Gujarat 01-09-2026 19:59 01-09-2026 23:32 03:33 18 0 0.02% 0.00% 80 952 64027 Complete outage of 220 kV Manza sub station On 01-09-2026, three protection-related operations occurred during First Time Charging and integration of the INGEL’s (IndianOil NTPC Green Energy Private Limited) equipment with the 220 kV Bus at Powerica Manza substation. At 19:59 hrs, TBC bay tripped during charging of INGEL’s transformer due to high inrush current. At 21:22 hrs, false Local Breaker Backup, LBB, operation during troubleshooting by INGEL resulted in tripping of 220 kV Jamkhambaliya-Manza-1 S/C, 220/33 kV Manza-ICT-1&2 owned by Powerica. Generation loss of 18 MW occurred at Manza Wind Power Plant due to loss of single evacuation path. 220 kV Jamkhambaliya-Manza-1 S/C was charged at 22:33 hrs. At 22:46 hrs, false Local Breaker Backup, LBB, operated again during troubleshooting by INGEL. 1. 220 kV Jamkhambaliya-Manza-1 S/C, 2. 220/33 kV Manza-ICT-1&2 | grid_india_gd/grid_events/2026-09-01
G00472 | 2026-09 | 16 | GD-1 | Gujarat | GJ | Western | 2026-09-02T05:47 | 2026-09-02T09:37 | 3.83 | 4 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss of 4 MW occurred at Zura S/S due to loss of evacuation path. | 2 GD-1 Gujarat 02-09-2026 05:47 02-09-2026 09:37 03:50 4 0 0.01% 0.00% 774 43 62429 Complete outage of 220 kV Zura sub station At 05:47 hrs/02-09-2026, 220kV Bhuj- Zura S/C line tripped at Bhuj end only on DT receipt. As the substation is Radial RE Plantly connected, 220kV Zura S/S went dark. Generation loss of 4 MW occurred at Zura S/S due to loss of evacuation path. 1. 220kV Bhuj Jhura S/C | grid_india_gd/grid_events/2026-09-01
G00473 | 2026-09 | 1 | GD-1 | Uttarakhand | UK | Northern | 2026-09-02T13:16 | 2026-09-02T14:02 | 0.77 | 0 | 187 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GD-1 Uttarakhand 02-09-2026 13:16 02-09-2026 14:02 00:46 0 187 0.00% 0 .25% 72805 76258 i)220/132kV Roorkee(UK) S/s has double main and transfer bus scheme at 220kV level. 220kV Roorkee(UK) is connected with 400/220 kV Roorkee(PG) & 220kV Nara(UP) through 220 kV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt | 1 GD-1 Uttarakhand 02-09-2026 13:16 02-09-2026 14:02 00:46 0 187 0.00% 0 .25% 72805 76258 i)220/132kV Roorkee(UK) S/s has double main and transfer bus scheme at 220kV level. 220kV Roorkee(UK) is connected with 400/220 kV Roorkee(PG) & 220kV Nara(UP) through 220 kV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt & 220 KV Nara(UP)-Roorkee(UK) (UP) Ckt respectively. ii)As reported, under antecedent system conditions, 220 KV Nara(UP)-Roorkee(UK) (UP) Ckt was tripped at 03:56 hrs on 02.09.2026 due to R-N phase to earth fault. As a result, 220 kV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt was the only source for 220kV Roorkee(UK) s/s. As per SCADA, 220 kV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt was carrying ~187 MW power from Roorkee(PG) to Roorkee(UK) station. iii)As reported, at 13:16 hrs, 220 KV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt tripped due to Y-N Phase to earth fault with fault current of Iy=2.17kA, and fault distance of 7.3KM from Roorkee(UK); fault was sensed in zone-2 from Roorkee(UK). iv)Tripping of the 220 kV Roorkee(PG)–Roorkee(UK)(PTCUL) ckt resulted in the blackout of 220kV Roorkee(UK). v)As per PMU at Roorkee(PG), Y-N Phase to earth fault was observed with fault clearance time of ~400 msec. vi)As per SCADA, change in demand of approx 187 MW was observed in UƩarakhand control area. 1)220 kV Roorkee(PG)-Roorkee(UK) (PTCUL) Ckt-1 | grid_india_gd/grid_events/2026-09-01
G00474 | 2026-09 | 2 | GI-2 | Haryana | HR | Northern | 2026-09-04T18:10 | 2026-09-04T19:23 | 1.22 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 2 GI-2 Haryana 04-09-2026 18:10 04-09-2026 19:23 01:13 0 0 0.00% 0.00% 545 90 70027 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2540 MW of power from Champa to Kurukshetra (~635 MW on each pole) (as per SCADA). ii)As reported, at 18:10 hrs, Po | 2 GI-2 Haryana 04-09-2026 18:10 04-09-2026 19:23 01:13 0 0 0.00% 0.00% 545 90 70027 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2540 MW of power from Champa to Kurukshetra (~635 MW on each pole) (as per SCADA). ii)As reported, at 18:10 hrs, Pole-2 of 800 kV HVDC Champa–Kurukshetra blocked due to false INBS current value in Lane-2, which resulted in latching of DC Differential Protection in Main-1 and Main-2 of Lane-2. Following blocking o f Pole-2, one of the associated disconnectors at Champa(WR) end failed to open; as a result, “Failed to Deparallel” alarm raised. Consequently, CAT-B protection was in itiated, and Pole-4 was blocked at 18:11 hrs. iii)As per the PMU at Kurukshetra(PG), no fault was observed; however, fluctuation in voltage was observed. iv)As per SCADA, no change in demand was observed in the Haryana control area, and no significant change in the power order was observed, as the power flow shifted to the other two poles. 1) 800 KV HVDC Kurukshetra(PG) Pole-2 2) 800 KV HVDC Kurukshetra(PG) Pole-4 | grid_india_gd/grid_events/2026-09-01
G00475 | 2026-09 | 20 | GD-1 | Madhya Pradesh | MP | Western | 2026-09-04T18:15 | 2026-09-04T19:17 | 1.03 | 2054 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 3 GD-1 Madhya Pradesh 04-09-2026 18:15 04-09-2026 19:17 01:02 2054 0 2.41% 0.00% 85199 65323 Elements Tripped Details of Grid Events during the Month of September 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of September 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) | grid_india_gd/grid_events/2026-09-01
G00476 | 2026-09 | 3 | GI-2 | Haryana | HR | Northern | 2026-09-04T18:42 | 2026-09-04T19:44 | 1.03 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 3 GI-2 Haryana 04-09-2026 18:42 04-09-2026 19:44 01:02 0 0 0.00% 0.00% 546 92 69123 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2540 MW of power from Champa to Kurukshetra (~1270 MW each on Pole-1 & Pole-3) (as per SCADA). Pole-2 & Pole-4 were | 3 GI-2 Haryana 04-09-2026 18:42 04-09-2026 19:44 01:02 0 0 0.00% 0.00% 546 92 69123 i)During the antecedent conditions, the 800 kV HVDC Champa–Kurukshetra link was carrying a total of ~2540 MW of power from Champa to Kurukshetra (~1270 MW each on Pole-1 & Pole-3) (as per SCADA). Pole-2 & Pole-4 were tripped during the 18:10 hrs event. ii)At 18:42 hrs, Pole-1 and Pole-3 of 800 kV HVDC Champa–Kurukshetra were blocked due to initiation of CAT-B protection. As reported, Bipole-1 Lane-1 was changed over from Lane-2 to resolve bit overflow and stalled communication i ssue. However, Lane-1 took 3.24 sec to become active, resulting in delay in communication between Bipole- 1, Bipole-2 and Master control. Subsequently, Bipole-2 declared its optical link to Bipole-1 faulty, resulting in initiation o f CAT-B signal in Pole-1 and Pole-3. iii)As per the PMU at Kurukshetra (PG), no fault was observed; however, fluctuation in voltage was observed. iv)As per SCADA, no change in demand was observed in the Haryana control area, and ~2540 MW change in the power order was observed. 1) 800 KV HVDC Kurukshetra(PG) Pole-1 2) 800 KV HVDC Kurukshetra(PG) Pole-3 | grid_india_gd/grid_events/2026-09-01
G00477 | 2026-09 | 47 | GI-1 | Odisha | OD | Eastern | 2026-09-05T07:58 | 2026-09-05T08:49 | 0.85 | 0 | 65 | FALSE | FALSE | FALSE | FALSE | FALSE | 1 GI-1 Odisha 05-09-2026 07:58 05-09-2026 08:49 00:51 0 65 0.00% 0.25% 347 47 25583 At 07:58 Hrs on 05.09.2026, the B-phase pipe bus conductor of the 220 kV Meramundali–Narsingpur line broken, resulting in a fault on Main Bus-2 at 220 kV Meramundali S/s. Consequently, all elements connected to Main | 1 GI-1 Odisha 05-09-2026 07:58 05-09-2026 08:49 00:51 0 65 0.00% 0.25% 347 47 25583 At 07:58 Hrs on 05.09.2026, the B-phase pipe bus conductor of the 220 kV Meramundali–Narsingpur line broken, resulting in a fault on Main Bus-2 at 220 kV Meramundali S/s. Consequently, all elements connected to Main Bus-2 and Main Bus-1(bus coupler tripped to isolate the fault, but the B-phase pole of the bus coupler breaker mechanically failed to open) tripped from the Meramundali end in Z-4 protection, as busbar protection was not available. As a result, the 220 kV Meramundali S/s became dead, leading to a total load loss of approximately 65 MW at Meramundali S/s. 400KV/220KV 315 MVA ICT 1 AT MEERAMUNDALI 400KV/220KV 315 MVA ICT 2 AT MEERAMUNDALI 220KV-TSTPP-MEERAMUNDALI-1 220KV-TSTPP-MEERAMUNDALI-2 | grid_india_gd/grid_events/2026-09-01
G00478 | 2026-09 | 19 | GD-1 | Gujarat | GJ | Western | 2026-09-06T05:03 | 2026-09-06T22:51 | 17.8 | 25 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 25 MW occurred at 220/33kV Nanavalka substation due to loss of the evacuation path. | 6 GD-1 Gujarat 06-09-2026 05:03 06-09-2026 22:51 17:48 25 0 0.03% 0.00% 79 413 64043 Complete outage of 220 kV Nanavalka sub station At 05:03 hr / 09.09.2026, 220KV-Nanavalka-Bhuj-1 S/C tripped due to B-phase to Earth fault. Generation loss of 25 MW occurred at 220/33kV Nanavalka substation due to loss of the evacuation path. As a result, 220kV Nana Valka sub-station Blacked out. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C 2. 220-kV Nanavalka-Alfanar- ICT-1 3. 220 kV Nanavalka-Alfanar- ICT-2 4. 220 kV Nanavalka-Alfanar- Bus-1 5. 220 kV Nanavalka-Alfanar- Bus-2 Complete outage of 400 kV Korba (NTPC) sub station At approximately 18:15 hrs on 04th September 2026, the 400 kV switchyard at NTPC Korba experienced a complete station blackout following the failure and blast of the Y-phase Circuit Breaker pole insulation in the 400 kV Korba–Birsingpur-1 bay. The incident occurred , during a check of isolator operation after rectification work on the breaker. while the bay was under planned shutdown for CRP–SAS migration and maintenance work. NTPC Reported that “During Circuit Breaker testing, the Y-pole DCRM was found abnormal and SF₆ gas purity was found low. A DILO machine was mobilised and rectification work was carried out. During the subsequent check of isolator closing operation, the Y-phase breaker insulation failed and the pole blasted, creating a fault connected to the 400 kV bus system.” 400 kV Korba-Birsingpur-1 bay was connected to Bus-3. Bus Section 13A connected Buses 1 and 3 | grid_india_gd/grid_events/2026-09-01
G00479 | 2026-09 | 17 | GD-1 | Gujarat | GJ | Western | 2026-09-06T08:27 | 2026-09-06T18:12 | 9.75 | 50 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 50 MW Occurred at Sidhpur (Torrent Power) due to loss of evacuation path. | 4 GD-1 Gujarat 06-09-2026 08:27 06-09-2026 18:12 09:45 50 0 0.06% 0.00% 79 675 68322 Complete outage of 220 kV Sidhpur (Torrent) sub station At 08:27 hrs / 06-09-2026, 220 kV Jamkhambaliya-Sidhpur-1 S/C tripped on R-E Fault. Auto-Reclose was attempted but was unsuccessful at the Jamkhambhaliya end. At the Sidhpur end, Main-I Zone-1 distance protection issued a three-pole trip. The Sidhpur Auto-Reclose cycle was initiated but subsequently inhibited following assertion of the Switch-On-To-Fault-related AR blocking signal. Damaged R-phase tension insulator at Tower No. 86 was found during patrolling. Generation loss of 50 MW Occurred at Sidhpur (Torrent Power) due to loss of evacuation path. 1. 220 kV Jamkhambaliya-Sidhpur-1 S/C | grid_india_gd/grid_events/2026-09-01
G00480 | 2026-09 | 18 | GD-1 | Maharashtra | MH | Western | 2026-09-06T12:25 | 2026-09-06T14:55 | 2.5 | 34 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of approx 34 MW was reported at Rahatani and Varasgaon. | 5 GD-1 Maharashtra 06-09-2026 12:25 06-09-2026 14:55 02:30 34 0 0.04% 0.0 0% 79400 70390 Complete outage of 220 kV Chinchwad sub station At 12:24 Hrs on 06.09.2026, the 22 kV Aksharland feeder at 220/132/100/22 kV Chinchwad-1 S/s tripped along with a major fire in the 22 kV switchyard; almost simultaneously the 22 kV Pimpri feeder tripped on a B-phase earth fault with bursting of its Current Transformers. The station's 110V DC system, already stressed with the entire CRP load riding on a single charger, failed to hold up under the fault-feeding condition, so the local protection at Chinchwad could not isolate the fault in time. Fault current continued to flow for well beyond the rated short-circuit withstand duration of the 22 kV switchgear, causing CTs/CBs of the Aksharland, Pimpri, Mahindra, GEC feeders and 80 MVA TF-8 to burst, and extensive fire/sparking in the Control Room Panels. The sustained fault was ultimately cleared only when the six source lines feeding the Chinchwad Bus (220 kV Urse, 220 kV Sahara, 132 kV Narayangaon, 132 kV Air-Inox, 132 kV Lonikand-2 and 132 kV Markal–Lonikand-2) tripped at their remote ends on backup over-current protection, resulting in a complete black-out of 220 kV Chinchwad-1 S/s and an associated loss of approximately 401 MW of load spread across Pimpri-Chinchwad, Pune city and Chakan/Talegaon industrial belt. Generation loss of approx 34 MW was reported at Rahatani and Varasgaon. 1 22 kV Aksharland Feeder (local) 2 22 kV Pimpri Feeder ( | grid_india_gd/grid_events/2026-09-01
G00481 | 2026-09 | 4 | GD-1 | Rajasthan | RJ | Northern | 2026-09-07T07:02 | 2026-09-07T12:13 | 5.18 | 242 | 0 | TRUE | FALSE | FALSE | TRUE | TRUE | vi)As per SCADA, a generation loss of approximately 242 MW at ASSPL(IP) was observed. | 4 GD-1 Rajasthan 07-09-2026 07:02 07-09-2026 12:13 05:11 242 0 0.46% 0.00 % 52323 65473 i)220 kV ASSPL(IP) has a double main bus scheme. Solar and BESS generation of ASSPL(IP) is evacuated through the 220 kV ASSPL_SL_BKN2-Bikaner_2(PBTSL) (ASSPL_BKN2) Ckt. ii)During antecedent conditions, as per SCADA, ASSPL(IP) was generating ~20 MW from solar and ~222 MW from BESS, with cumulative generation of ~242 MW being evacuated through the 220 kV ASSPL_SL_BKN2-Bikaner_2(PBTSL) (ASSPL_BKN2) Ckt. iii)As reported, at 07:02 hrs, the 400 kV Bikaner_2(PBTSL)-Bikaner_3(PBNTL) (P_Vataman_TL) Ckt-2 tripped due to a Y-N phase-to-earth fault, with a fault current of 1.6 kA from Bikaner_2 (PG) (exact location of the fault is yet to be shared). iv)As reported, at the same time, the 220 kV ASSPL_SL_BKN2-Bikaner_2(PBTSL) (ASSPL_BKN2) Ckt tripped due to a Y-N phase-to-earth fault. As per the DR at Bikaner_2(PG), the fault current was 29 kA, and the fault was sensed in Z-2 from Bikaner_2(PG). The fault distance was 2.19 km from Bikaner_2(PG). This led to a complete blackout of the 220 kV ASSPL(IP) station. v)As per the PMU at Bikaner_2(PG), a Y-N phase-to-earth fault was observed with a fault clearing time of 80 msec. vi)As per SCADA, a generation loss of approximately 242 MW at ASSPL(IP) was observed. 1) 400 KV Bikaner_2 (PBTSL)-Bikaner_3(PBNTL) (P_Vataman_TL) Ckt-2 2) 220 KV ASSPL_SL_BKN2-Bikaner_2 (PBTSL) (ASSPL_BKN2) Ckt-1 | grid_india_gd/grid_events/2026-09-01
G00482 | 2026-09 | 5 | GI-1 | Uttarakhand & Himachal Pradesh |  |  | 2026-09-07T14:46 | 2026-09-07T16:26 | 1.67 | 0 | 127 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, there was no load loss in Himachal control area, ~67 MW load loss in UƩarakhand control area, and there was no generation loss in Himachal or Uttarakhand control area. | 5 GI-1 Uttarakhand & Himachal Pradesh 07-09-2026 14:46 07-09-2026 16:26 01:40 0 127 0.00% 0.17% 70865 74674 i)220 kV Khodri(UK) Substation has a double main bus bar system with 4 x 60 MW generating units. 220/132 kV Majri(HP) has a double main bus scheme at both 220 kV & 132 kV levels, with 2 x 30 MW generating units connected at the 132 kV level. ii)During the antecedent condition, as reported, 220 kV Khodri(UK)-Majri(HP) (UK) CKT-1 and CKT-2 were carrying ~50 MW load each, and the 100 MVA 220/132 kV ICT at Khodri(UK) was not carrying any load. iii)As reported, at 14:46 hrs, 220 kV Khodri(UK)-Majri(HP) (UK) Ckt-2 tripped from Khodri(UK) end due to operation of directional earth fault protection due to a B-N phase- to-earth fault with a fault current of 2.2 kA from Khodri(UK) end (exact fault location is yet to be shared). iv)At the same time, 220 kV Khodri(UK)-Majri(HP) (UK) Ckt-1 tripped from Khodri(UK) end due to a B-N phase-to-earth fault with a fault current of 2.3 kA and a fault distance of 20.28 KM from Khodri(UK); the fault was sensed in Z-1 from Khodri(UK). v)At the same time, 100 MVA 220/132 kV ICT at Khodri(UK) also tripped due to the operation of earth fault protection. vi)As reported, tripping of 220 kV Khodri(UK)-Majri(HP) (UK) Ckt-1 and Ckt-2 resulted in ~60 MW load loss at Majri(HP). vii)As per PMU at Dehradun(PG), a B-N phase-to-earth fault was observed in the system, with delayed fault clearance of 400 msec. viii)As per SCADA, there was no load loss in Himac | grid_india_gd/grid_events/2026-09-01
G00483 | 2026-09 | 21 | GD-1 | Gujarat | GJ | Western | 2026-09-09T13:55 | 2026-09-09T20:04 | 6.15 | 76 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 76.4 MW Occurred at Chugger (SITAC) Wind Power Plant due to loss of evacuation path. | 7 GD-1 Gujarat 09-09-2026 13:55 09-09-2026 20:04 06:09 76 0 0.10% 0.00% 79 675 68322 Complete outage of 220 kV Chugger (SITAC) sub station At 13:55 hrs / 09-09-2026, 220 kV Bhuj II-Chugger-1 S/C tripped on B-E Fault. Failed 90 kN silicone-rubber composite insulator was found at tower location 01 during patrolling. Auto-Reclose was attempted but was unsuccessful at the Bhuj II end At the Chugger end, Main-I Zone-2 distance protection issued a three-pole trip. Auto-Reclose cycle was initiated but subsequently all three phases tripped following assertion of the Switch-On-To-Fault signal. Generation loss of 76.4 MW Occurred at Chugger (SITAC) Wind Power Plant due to loss of evacuation path. 1. 220 kV Bhuj II-Chugger-1 S/C | grid_india_gd/grid_events/2026-09-01
G00484 | 2026-09 | 22 | GD-1 | Gujarat | GJ | Western | 2026-09-09T13:55 | 2026-09-09T17:11 | 3.27 | 82 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | Generation loss of 4 MW occurred at Zura S/S due to loss of evacuation path. | 8 GD-1 Gujarat 09-09-2026 13:55 09-09-2026 17:11 03:16 82 0 0.09% 0.00% 94 805 75610 Complete outage of 220 kV Zura sub station At 13:55 hrs/09-09-2026, 220kV Bhuj- Zura S/C line tripped at Bhuj end only on DT receipt. As the substation is Radial RE Plantly connected, 220kV Zura S/S went dark. Generation loss of 4 MW occurred at Zura S/S due to loss of evacuation path. 1. 220kV Bhuj Jhura S/C | grid_india_gd/grid_events/2026-09-01
G00485 | 2026-09 | 48 | GI-2 | DVC | DV | Eastern | 2026-09-10T08:40 | 2026-09-10T11:10 | 2.5 | 850 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Total generation loss of 850 MW reported at Mejia S/s. | 2 GI-2 DVC 10-09-2026 08:40 10-09-2026 11:10 02:30 850 0 2.34% 0.00% 36344 25985 At 08:09 hrs on 10.09.2026, the station transformer-2 was shifted on transfer bus through the transfer bus coupler (from Main bus-I) to facilitate maintenance work for attending to oil/air leakage. At 08:40 hrs, the R-phase string insulator of the transfer bus at the line gantry burst, resulting in the tripping of Main Bus-2 at Mejia. Consequently, all elements connected to Main Bus-2 (400kV Mejia–Jamshedpur Ckt-1, 400kV Mejia–Maithon Ckt-2, and Mejia Unit #7, ST#2) also tripped. At the same time Unit #8 also tripped due to tripping of its associated Station transformer (ST#2). Total generation loss of 850 MW reported at Mejia S/s. 400KV-JAMSHEDPUR-MEJIA-1 400KV-MAITHON-MEJIA-2 Mejia Unit-7 (500 MW) Mejia Unit-8 (500 MW) Main Bus-2 at Mejia | grid_india_gd/grid_events/2026-09-01
G00486 | 2026-09 | 6 | GI-2 | Uttar Pradesh | UP | Northern | 2026-09-10T13:54 | 2026-09-10T14:10 | 0.27 | 0 | 99 | FALSE | FALSE | FALSE | FALSE | FALSE | 6 GI-2 Uttar Pradesh 10-09-2026 13:54 10-09-2026 14:10 00:16 0 99 0.00% 0 .12% 73740 80402 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)Under antecedent conditions, as reported, 220 KV Gorakhpur- Hata (UP) Ckt-2, 220 KV Gorakhpur- Gorakhpu | 6 GI-2 Uttar Pradesh 10-09-2026 13:54 10-09-2026 14:10 00:16 0 99 0.00% 0 .12% 73740 80402 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)Under antecedent conditions, as reported, 220 KV Gorakhpur- Hata (UP) Ckt-2, 220 KV Gorakhpur- Gorakhpur New (UP) Ckt-1, 220 KV Gorakhpur- Khorabar (UP) Ckt-1, 400/220 kV 500 MVA ICT 1 at Gorakhpur(UP), and 400/220 kV 315 MVA ICT 3 at Gorakhpur(UP) were connected with 220kV Bus-1. 220 KV Gorakhpur- Hata (UP) Ckt-1, 220 KV Gorakhpur- Gorakhpur New (UP) Ckt-2, 220 KV Gorakhpur- Gorakhpur2 (UP) Ckt-1, and 400/220 kV 500 MVA ICT 2 at Gorakhpur(UP) were connected with 220kV Bus-2. As per SCADA, loading of ICT-1, ICT-2, and ICT-3 were ~232 MW, ~215 MW, & ~147 MW, respectively. 220 KV Gorakhpur- Deora (UP) Ckt was under outage. iii)As reported, at 13:54 hrs, while charging 220 KV Gorakhpur- Deora (UP) Ckt, bus bar differential protection of bus-2 operated, as earth switch was not opened before closing bus-side isolator, result ed in tripping of Bus-2 along with all the elements connected with it (exact reason for opera tion of bus bar protection is yet to be shared). iv)As per PMU at Lucknow(PG), Y-N phase to earth fault was observed with fault clearing time of 80 msec. v)As per SCADA, change in demand of approx 99 MW was observed in UP control area. 1) 220 KV Gorakhpur- Hata (UP) Ckt-1 2) 220 KV Gorakhpur- Gorakhpur New (UP) Ckt-2 3) 220 KV Gorakhpur- Gorakhpur2 (UP) Ckt-1 4) 400/220 kV 5 | grid_india_gd/grid_events/2026-09-01
G00487 | 2026-09 | 7 | GD-1 | Uttar Pradesh | UP | Northern | 2026-09-10T14:12 | 2026-09-10T15:16 | 1.07 | 0 | 501 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 7 GD-1 Uttar Pradesh 10-09-2026 14:12 10-09-2026 15:16 01:04 0 501 0.00% 0.62% 73736 80653 i)400/220kV Gorakhpur(UP) has double main and transfer bus scheme at both 400kV level and 220kV level. ii)Under antecedent conditions, as reported, after the event on 13:54 hrs, Bus-2 was charged with 220 KV Gorakhpur- Gorakhpur2 (UP) Ckt-1 and 220 KV Gorakhpur- Hata (UP) Ckt-1; however bus coupler was still out resulted in split bus operation at 220kV Gorakhpur(UP). 400/220kV 500 MVA ICT-2 which was tripped during 13:54 hrs event was still under outage. 220 KV Gorakhpur- Hata (UP) Ckt-2, 220 KV Gorakhpur- Gorakhpur New (UP) Ckt-1, 220 KV Gorakhpur- Khorabar (UP) Ckt-1, 400/220 kV 500 MVA ICT 1 at Gorakhpur(UP), and 400/220 kV 315 MVA ICT 3 at Gorakhpur(UP) were connected with 220kV Bus-1. Loadings of ICT-1 and ICT-3 were ~312 MW and ~198 MW, respectively. iii)As reported, at 14:12 hrs, while synchronizing 220kV Main Bus-1 to 220kV Main Bus-2, heavy flashing occurred on LV side isolator of ICT-3, which led to operation of Bus- bar protection, as a result 220kV Bus-1 and 220kV Main Bus-2 tripped, led to the tripping of all 220kV elements. iv)Further, it was reported that the HV-side CB of the 315 MVA ICT-III opened with a delay, resulting in the operation of the LBB protection. Consequently, the elements connected to the 400 kV Main Bus-I also tripped. These cascadin g trippings ultimately resulted in a blackout of the 400 kV S/S Gorakhpur. v)As per at Lucknow(PG), R-N phase to earth fau | grid_india_gd/grid_events/2026-09-01
G00488 | 2026-09 | 23 | GD-1 | Gujarat | GJ | Western | 2026-09-11T10:53 | 2026-09-11T11:56 | 1.05 | 101 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 101 MW occurred at Shajapur U6 due loss of evacuation path and station became dark. | 9 GD-1 Gujarat 11-09-2026 10:53 11-09-2026 11:56 01:03 101 0 0.11% 0.00% 9 2365 77908 Complete outage of 220 kV Burlay sub station At 10:53 Hrs/11-09-2026, 220kV Shajapur (Dehripal U7) -Shajapur (Burlay U6) line tripped due to LA failure. Generation loss of 101 MW occurred at Shajapur U6 due loss of evacuation path and station became dark. 1 . 220kV Shajapur U7 (Dehripal) -Shajapur U6 (Burley) line 2. 220KV/33KV SHAJAPUR Unit-6(Burley)-ICT-1 | grid_india_gd/grid_events/2026-09-01
G00489 | 2026-09 | 8 | GD-1 | Rajasthan | RJ | Northern | 2026-09-11T14:51 | 2026-09-11T18:29 | 3.63 | 154 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | vi)As per SCADA, generation loss of approx 154 MW at KREPL(IP) was observed. | 8 GD-1 Rajasthan 11-09-2026 14:51 11-09-2026 18:29 03:38 154 0 0.21% 0.00 % 71647 79170 i)220kV KREPL(IP) has double main bus scheme. Generation of KREPL(IP) evacuated through 220 KV Bikaner_2 (PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt. ii)During antecedent conditions, as per SCADA, KREPL(IP) was generating ~154 MW. iii)As reported, at 14:51 hrs, 220 KV Bikaner_2(PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt tripped due to operation of differential protection at both ends due to B-N phase to earth fault with fault current of 1.82kA at Bikaner_2( PG) end (exact location of fault is yet to be shared). As per D R at Bikaner_2(PG) end, AR attempt was successful at Bikaner_2(PG) end. iv)This tripping led to complete blackout of 220kV KREPL(IP) station. v)As per PMU at Bikaner_2(PG), B-N phase to earth fault was observed with fault clearing time of 80 msec. vi)As per SCADA, generation loss of approx 154 MW at KREPL(IP) was observed. 1) 220 KV Bikaner_2 (PBTSL)-KHIDRAT_REPL_SL_BKN2 (KHIDRAT_REPL) Ckt-1 | grid_india_gd/grid_events/2026-09-01
G00490 | 2026-09 | 44 | GI-1 | Karnataka | KA | Southern | 2026-09-12T01:59 | 2026-09-12T02:50 | 0.85 | 488 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-1 KARNATAKA 12-09-2026 01:59 12-09-2026 02:50 00:51 488 0 0.98% 0.00 % 49609.59 53136.86 Tripping of 220kV Bus-1 of 220kV Sharavathy PH of KPCL As per the reports submitted, the triggering incident was B-G fault in 220kV Sharavathy Belgavi line. At the same time, Sharavathy Unit-6 tripped on o | 17 GI-1 KARNATAKA 12-09-2026 01:59 12-09-2026 02:50 00:51 488 0 0.98% 0.00 % 49609.59 53136.86 Tripping of 220kV Bus-1 of 220kV Sharavathy PH of KPCL As per the reports submitted, the triggering incident was B-G fault in 220kV Sharavathy Belgavi line. At the same time, Sharavathy Unit-6 tripped on over current protection maloperation , but the Unit-6 breaker failed to open. This led to operation of Unit-6 LBB and all elements connected to 220kV Sharavathy Bus-1 tripped. This led to loss of power supply to 220kV Bus-1 of 220kV Sharavathy PH 220KV-SHIRALKOPPA-SHARAVATHY-1, 220KV-SIRSI- SHARAVATHY-1, 220KV-SIRSI-SHARAVATHY-2, 220KV- SHARAVATHY-TALGUPPA-2, 220KV-MRS SHIMOGA- SHARAVATHY-3, 220KV-SHARAVATHY-MRS SHIMOGA-2 | grid_india_gd/grid_events/2026-09-01
G00491 | 2026-09 | 26 | NEAR MISS INCIDENT | Gujarat | GJ | Western | 2026-09-13T12:53 | 2026-09-13T13:12 | 0.32 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | As a response to the voltage drop, the Renewable Generators at Khavda complex and Bhuj experienced LVRT. | 12 Near Miss Incident Gujarat 13-09-2026 12:53 13-09-2026 13:12 00:19 0 0 0.00% 0.00% 77937 66 417 Near Miss Incident at of 765 kV Lakadia sub station At 1253 Hrs on 14th September 2026, at 765kV Lakadiya S/S 6 nos of transmission lines tripped from remote end only and were holding at 765kV Lakadiya S/S (As confirmed through SCADA SOE & PMU Line Phase Currents), the reason for tripping of the transmission lines as informed by POWERGRID is DT received from 765kV Lakadiya SS. However, based on the 765kV Lakadiya Positive Sequence Voltage of all the above line, it was observed that voltage were below the Over-voltage threshold. After tripping of the transmission lines, the Khavda complex witnessed a voltage drop from 405kV to 340kV triggering LVRT operation (due to tripping of 6 nos of transmission lines). TPCL (5x800 MW) and Gandhinagar TPS reported hunting in their generators during the incident. Increased bus angle (15 degree increase) was observed between KPS-1 to Bhuj. As a response to the voltage drop, the Renewable Generators at Khavda complex and Bhuj experienced LVRT. No tripping of RE inverters or WTG was reported during the incident. oscillation in reactive power/voltage was observed from 12:53 hrs to 13:17 hrs. This oscillation got reduced when the 765kV lines were charged i.e. 765kV Lakadiya – Bhuj 2 – 1 at 13:12 and 765kV Lakadiya – KPS 2 -1 at 13:17 hrs. 1. 765kV Lakadiya–Banaskantha-1 & 2 2. 1. 765kV Lakadiya–Khavda PS2-1 & 2 3. 1. 765kV Lakadiya–Bhuj II-1&2 | grid_india_gd/grid_events/2026-09-01
G00492 | 2026-09 | 24 | GD-1 | Gujarat | GJ | Western | 2026-09-13T17:43 | 2026-09-13T18:37 | 0.9 | 132 | 0 | FALSE | TRUE | FALSE | FALSE | TRUE | Generation loss of 132 MW Occurred at Chugger (SITAC) Wind Power Plant due to loss of evacuation path. | 10 GD-1 Gujarat 13-09-2026 17:43 13-09-2026 18:37 00:54 132 0 0.16% 0.00% 8 0952 64027 Complete outage of 220 kV Chugger (SITAC) sub station At 17:43 hrs / 13-09-2026, 220 kV Bhuj II-Chugger-1 S/C tripped on R-E Fault. No abnormalities were found during patrolling. Auto-Reclose was successful at the Bhuj II end. At the Chugger end, Zone-1 distance protection issued a three-pole trip. Auto-Reclose cycle was initiated but subsequently all three phases tripped following assertion of the Switch-On-To-Fault signal. Generation loss of 132 MW Occurred at Chugger (SITAC) Wind Power Plant due to loss of evacuation path. 1. 220 kV Bhuj II-Chugger-1 S/C | grid_india_gd/grid_events/2026-09-01
G00493 | 2026-09 | 25 | GD-1 | Gujarat | GJ | Western | 2026-09-13T18:45 | 2026-09-17T23:51 | 101.1 | 50 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 50 MW occurred at 220/33kV Nanavalka substation due to loss of the evacuation path as a result, 220kV Nana Valka sub-station Blacked out. | 11 GD-1 Gujarat 13-09-2026 18:45 17-09-2026 23:51 101:06 50 0 0.06% 0.00% 8 0660 65049 Complete outage of 220 kV Nanavalka sub station At 18:45 Hrs/ 13-09-2026, 220KV-Nanavalka-Bhuj-1 S/C tripped due to R-phase to Earth fault. Generation loss of 50 MW occurred at 220/33kV Nanavalka substation due to loss of the evacuation path as a result, 220kV Nana Valka sub-station Blacked out. 1. 220 kV Bhuj- Nanavalka(Alfanar) S/C 2. 220 kV Bhuj- Nanavalka(Alfanar) 3 .220 kV Bhuj- Nanavalka(Alfanar) 4 .220 kV Bhuj- Nanavalka(Alfanar) | grid_india_gd/grid_events/2026-09-01
G00494 | 2026-09 | 27 | GI-1 | Maharashtra | MH | Western | 2026-09-15T09:11 | 2026-09-15T10:11 | 1 | 215 | 12 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GI-1 Maharashtra 15-09-2026 09:11 15-09-2026 10:11 01:00 215 12 0.28% 0 .02% 76412 63825 Partial outage at 220 kV Chandrapur sub station At 09:11:58 hrs on 15-09-2026, an R-phase to earth fault occurred on 220 kV Chandrapur–Sicom Ckt-2, about 7.85 km from the Chandrapur (GCR) end. The Zone-1 dist | 13 GI-1 Maharashtra 15-09-2026 09:11 15-09-2026 10:11 01:00 215 12 0.28% 0 .02% 76412 63825 Partial outage at 220 kV Chandrapur sub station At 09:11:58 hrs on 15-09-2026, an R-phase to earth fault occurred on 220 kV Chandrapur–Sicom Ckt-2, about 7.85 km from the Chandrapur (GCR) end. The Zone-1 distance relay picked up and issued the R-pole trip command straight away, but the R-pole of the ABB circuit breaker did not clear the fault and the fault current kept flowing for about 0.33 s. The LBB scheme of 220 kV Bus-1 then operated and tripped every element connected to Bus-1, including the bus coupler. 400/220 kV, 315 MVA ICT-1 (on Bus-2) also tripped on Oil Surge Relay which was undesirable. With 220 kV Station Transformer-2 gone, the auxiliary supply of Unit-3 and Unit-4 was lost; GTR-4 tripped on low drum level at 09:27 hrs and GTR-3 was hand tripped at 09:40 hrs, which took out about 215 MW of generation. MSETCL reported a load loss of 12 MW. No LTS/SPS operation was reported. 1. 220 kV Chandrapur Bus-1 2. 220 kV Sicom Ckt-2 3. 220 kV Bus-coupler 4. 220 kV Station Tf-2 5. 400/220/33 kV, 315 MVA ICT-2 6. 220 kV Grace 7. 220 kV Chandrapur-2 8. 220/33 kV, 50 MVA Transformer 9. 220 kV Wani 10 220 kV TSS Ckt-2 11. 400/220/33 kV, 315 MVA ICT-1 (Bus-2) 12. 400 kV GTR-4 (Unit-4) 13. 400 kV GTR-3 (Unit-3) | grid_india_gd/grid_events/2026-09-01
G00495 | 2026-09 | 9 | GD-1 | Haryana | HR | Northern | 2026-09-15T17:37 | 2026-09-16T01:36 | 7.98 | 0 | 80 | FALSE | FALSE | FALSE | FALSE | FALSE | 9 GD-1 Haryana 15-09-2026 17:37 16-09-2026 01:36 07:59 0 80 0.00% 0.11% 59 409 74233 i)During the antecedent conditions, the 500 kV HVDC Mundra–Mahindergarh(APL) was transmiƫng a total of ~1520 MW from Mundra(WR) to Mahindergarh(NR), with ~760 MW on each pole (as per SCADA). ii)As reported, at 17:30 | 9 GD-1 Haryana 15-09-2026 17:37 16-09-2026 01:36 07:59 0 80 0.00% 0.11% 59 409 74233 i)During the antecedent conditions, the 500 kV HVDC Mundra–Mahindergarh(APL) was transmiƫng a total of ~1520 MW from Mundra(WR) to Mahindergarh(NR), with ~760 MW on each pole (as per SCADA). ii)As reported, at 17:30 hrs, Pole-2 of the 500 kV HVDC Mundra–Mahindergarh(APL) tripped from the Mundra(WR) end due to the loss of both sources of auxiliary supply. Following the tripping of Pole-2, there was no change in the po wer order, as the entire power was transferred to Pole-1. Since the capacity of a single pole is 1250 MW, the power order was gradually reduced and reached ~1278 MW at 17:37 hrs. iii)At 17:37 hrs, Pole-1 of the 500 kV HVDC Mundra–Mahindergarh was blocked. As reported by APL, the electrode line conductor was broken between Towers 353 and 354. Consequently, the “Electrode Line Protection 60EL – Prewarning” and “Electrode Line Protection 60EL-2 – Forced Retard” alarms were initiated, resulting in the blocking of Pole-1 of the 500 kV HVDC Mundra–Mahindergarh. iv)As reported by APL, the SPS Case-2 signal was sent to all configured load stations from the Mahindergarh(APL) end. However, only Rajasthan reported load relief of ~80 MW, due to the tripping of the 132 kV Alwar–Ramgarh Ckt, 132 kV Alwar–TELCO Ckt, and 132 kV Ratangarh–Sadarsahar Ckt. SLDC Haryana reported the tripping of 220 kV Dhanonda–Lula Ahir Ckt-1 and Ckt-2; however, no load relief was observed due to these trippings. No | grid_india_gd/grid_events/2026-09-01
G00496 | 2026-09 | 28 | GI-1 | Madhya Pradesh | MP | Western | 2026-09-16T12:10 | 2026-09-16T13:45 | 1.58 | 160 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of around 160 MW occurred due to loss of evacuation path. | 14 GI-1 Madhya Pradesh 16-09-2026 12:10 16-09-2026 13:45 01:35 160 0 0.20% 0.00% 80610 63616 Partial outage at 220 kV Baradwada sub station At 12:10 Hrs/16-09-2026, 220/33 kV Baradwada (Neemuch Unit-1) ICT-1 and ICT-2 tripped due to O/C in B-ph and O/C in Y-ph respectively. Generation loss of around 160 MW occurred due to loss of evacuation path. 1 . 220/33 kV Baradwada (Neemuch Unit-1) ICT-1 2. 220/33 kV Baradwada (Neemuch Unit-1) ICT-2 | grid_india_gd/grid_events/2026-09-01
G00497 | 2026-09 | 30 | GD-1 | Gujarat | GJ | Western | 2026-09-17T03:07 | 2026-09-17T20:07 | 17 | 172 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of around 172 MW occurred due to loss of evacuation path. | 16 GD-1 Gujarat 17-09-2026 03:07 17-09-2026 20:07 17:00 172 0 0.22% 0.00% 7 7443 62429 Complete outage of 400 kV Khavda PSS14 sub station At 03:07:40 hrs/ 17 Sep 2026, 400 kV KPS-PSS-12 line tripped due to the operation of Y-phase Line Differential Protection. Generation loss of around 172 MW occurred due to loss of evacuation path. 1. 400 kV KPS-PSS-12 2. 400 kV KPS-PSS-14 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) Elements Tripped Details of Grid Events during the Month of September 2026 in Western Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) | grid_india_gd/grid_events/2026-09-01
G00498 | 2026-09 | 29 | GD-1 | Gujarat | GJ | Western | 2026-09-17T10:36 | 2026-09-18T21:36 | 35 | 131 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of around 131 MW occurred due to loss of evacuation path. | 15 GD-1 Gujarat 17-09-2026 10:36 18-09-2026 21:36 35:00 131 0 0.16% 0.00% 8 4300 68217 Complete outage of 220 kV Khakharda (Apraava) sub station At 10:36 Hrs/17-09-2026, 220KV Jamkhambaliya – Khakharda Line tripped due to distance protection at Jamkhambaliya and Earth Fault at Khakharda respectively. Generation loss of around 131 MW occurred due to loss of evacuation path. 1. 220KV Jamkhambaliya – Khakharda | grid_india_gd/grid_events/2026-09-01
G00499 | 2026-09 | 45 | GI-1 | ANDHRA PRADESH , TELANGANA |  |  | 2026-09-18T19:17 | 2026-09-19T03:56 | 8.65 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | 18 GI-1 ANDHRA PRADESH , TELANGANA 18-09-2026 19:17 19-09-2026 03:56 08:39 0 0 0.00% 0.00% 54025.75 59409. 73 Tripping of 220kV Bus-1 of 220kV Nagarjunsagar_AP(Tallapalli SWS) of APTRANSCO As per the reports submitted, the triggering incident was failure of Y-phase disc insulator near 220kV Nagarjun | 18 GI-1 ANDHRA PRADESH , TELANGANA 18-09-2026 19:17 19-09-2026 03:56 08:39 0 0 0.00% 0.00% 54025.75 59409. 73 Tripping of 220kV Bus-1 of 220kV Nagarjunsagar_AP(Tallapalli SWS) of APTRANSCO As per the reports submitted, the triggering incident was failure of Y-phase disc insulator near 220kV Nagarjunsagar_AP(Tallapalli SWS) Bus-1 causing Y-G fault in the Bus. Immediately, 220kV Bus-1 BBP operated and all elements connected to the bus tripped. 220KV-NAGARJUNASAGAR_AP-CHALAKURTHY-1, 220KV- NAGARJUNASAGAR_AP-RENTACHINTHALA-2, 220KV- NAGARJUNASAGAR_AP-INAPARAJUPALLI-1, NAGARJUNASAGAR_AP - 220KV | grid_india_gd/grid_events/2026-09-01
G00500 | 2026-09 | 49 | GD-1 | Sikkim | SK | Eastern | 2026-09-19T14:29 | 2026-09-19T17:25 | 2.93 | 487 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Total generation loss of 487 MW reported at Teesta V S/s. | 3 GD-1 Sikkim 19-09-2026 14:29 19-09-2026 17:25 02:56 487 0 1.50% 0.00% 3 2532 29340 At 14:29 hrs on 19.09.2026, a high resistive fault was occurred in 400kV Rangpo-Binaguri-2 line and delayed fault clearance from Rangpo end. At the same time 400kV Teesta V- Rangpo Ckt 1 & 2 tripped due to operation of DEF from Teesta V end and DT Received at Rangpo end. Due to tripping of 400kV Rangpo-Teesta V D/C, all running units at Teesta V got tripped due to loss of evacuation path and 400kV Teesta V S/s became dead. Total generation loss of 487 MW reported at Teesta V S/s. 400kV-Teesta V- Rangpo-1 400kV-Teesta V- Rangpo-2 Teesta V Unit-1(170 MW) Teesta V Unit-2(170 MW) Teesta V Unit-3(170 MW) | grid_india_gd/grid_events/2026-09-01
G00501 | 2026-09 | 31 | GI-1 | Gujarat | GJ | Western | 2026-09-19T18:01 | 2026-09-19T18:37 | 0.6 | 0 | 800 | FALSE | FALSE | FALSE | FALSE | FALSE | 17 GI-1 Gujarat 19-09-2026 18:01 19-09-2026 18:37 00:36 0 800 0.00% 1.18% 8 2315 68063 Partial outage at 220 kV Haldarwa sub station At 18:01 Hrs./ 19.09.2026 220kV Haldarwa bus-2 tripped due to 220kV Jhanor-Haldarwa-2 line CT jumper opened and fell on bus. Approx 800 MW load loss occurred in Gujara | 17 GI-1 Gujarat 19-09-2026 18:01 19-09-2026 18:37 00:36 0 800 0.00% 1.18% 8 2315 68063 Partial outage at 220 kV Haldarwa sub station At 18:01 Hrs./ 19.09.2026 220kV Haldarwa bus-2 tripped due to 220kV Jhanor-Haldarwa-2 line CT jumper opened and fell on bus. Approx 800 MW load loss occurred in Gujarat control area and ~900 MW demand drop observed in Gujarat’s demand plot. 1. 220kV Haldarwa Bus-2 2. 220kV Jhanor-Haldarwa-1 3. 220kV Jhanor-Haldarwa-2 4. 220kV Kawas-Haldarwa-2 5. 220kV Kaps-Haldarwa-2 6. 220kV GPEC-Haldarwa-2 7. 220kV Haldarwa-Dahej-1 8. 220kV Haldarwa-Wagra-1 9. 220kV Haldarwa-Dahej-2 10. 220/66kV Haldarwa ICT-1 11. 220/132kV Haldarwa ICT-3 | grid_india_gd/grid_events/2026-09-01
G00502 | 2026-09 | 33 | GD-1 | Madhya Pradesh | MP | Western | 2026-09-20T08:43 | 2026-09-20T11:13 | 2.5 | 170 | 0 | TRUE | FALSE | FALSE | FALSE | TRUE | Generation loss of 170 MW occured at Bhawsingpura and Kanwani (Solar power) plant due to loss of evacuation path. | 19 GD-1 Madhya Pradesh 20-09-2026 08:43 20-09-2026 11:13 02:30 170 0 0.22% 0.00% 76412 63825 Complete outage of 220 kV Kanwani (Masaya Solar) sub station At 08:43 hrs / 20-09-2026, 220 kV Khandwa-Bhawsingpura-1 S/C tripped on Under voltage stage-2 protection due to a fault in the cable between the CRP panel and the CVT JB of secondary winding in the R-phase of the CVT, which resulted in a voltage drop in the R-phase. Generation loss of 170 MW occured at Bhawsingpura and Kanwani (Solar power) plant due to loss of evacuation path. 1. 220 kV Khandwa-Bhawsingpura-1 S/C 2. 220 kV Bhawsingpura-Kanwani-1 S/C | grid_india_gd/grid_events/2026-09-01
G00503 | 2026-09 | 11 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-09-20T11:42 | 2026-09-20T20:56 | 9.23 | 0 | 142 | FALSE | FALSE | FALSE | FALSE | FALSE | 11 GI-1 Jammu and Kashmir 20-09-2026 11:42 20-09-2026 20:56 09:14 0 142 0.00% 0.20% 67083 70933 i)220/132 kV Gladni(JK) S/s has a double-main-bus scheme at 220 kV. The 220 kV Gladni(JK) S/s is connected to Salal(NH) through 220 kV Salal(NH)-Gladni(JK) (PG) Ckt-1 and Ckt-2, and to 220 kV Chowadhi(JK) | 11 GI-1 Jammu and Kashmir 20-09-2026 11:42 20-09-2026 20:56 09:14 0 142 0.00% 0.20% 67083 70933 i)220/132 kV Gladni(JK) S/s has a double-main-bus scheme at 220 kV. The 220 kV Gladni(JK) S/s is connected to Salal(NH) through 220 kV Salal(NH)-Gladni(JK) (PG) Ckt-1 and Ckt-2, and to 220 kV Chowadhi(JK) through the 220 kV Chowadhi-Gladni (JK) Ckt. ii)Under the antecedent condition, as reported, 220 kV Gladni(JK) S/s was operating in bus-split mode. 220 kV Salal(NH)-Gladni(JK) (PG) Ckt-1 and Ckt-2, 220/132 kV, 150 MVA ICT-1, and 220/132 kV, 400 MVA ICT-3 were connected to Bus-1, while the 220 kV Chowadhi(JK)-Gladni(JK) Ckt and 220/132 kV, 160 MVA ICT-2 were connected to Bus-2. Both 220 kV buses were feeding separate loads. 220 kV Chowadhi(JK)-Gladni(JK) Ckt was carrying ~140 MW from Chowadhi(JK) towards Gl adni(JK). iii)As reported, at 11:42 hrs, the 220 kV Chowadhi(JK)-Gladni(JK) Ckt tripped due snaping of conductor (exact fault details, nature of protection operated, and location of fault is yet to be shared). Due to the bus-split operation at Gladni(JK), tripping of this line resulted in load loss. iv)As per the PMU at Kishenpur(PG), a Y-N phase-to-earth fault followed by another Y-N phase-to-earth fault was observed, with a fault-clearing time of 80 msec in both cases. v)As per SCADA, a change in demand of ~142 MW was observed in the J&K Control Area. 1) 220 KV Chowadhi (JK)-Gladni(PDD) (PDD JK) Ckt-1 | grid_india_gd/grid_events/2026-09-01
G00504 | 2026-09 | 32 | GD-1 | Gujarat | GJ | Western | 2026-09-20T16:09 | 2026-09-20T22:45 | 6.6 | 80 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 80 MW occurred due to loss of evacuation path at Tebhada Welspun S/S. | 18 GD-1 Gujarat 20-09-2026 16:09 20-09-2026 22:45 06:36 80 0 0.10% 0.00% 81 135 64489 Complete outage of 220 kV Tebhada (Welspun) sub station At 16:09 Hrs, 220kV-Tebhada Welspun- Jamkhambalia line tripped on Rph-E fault. Generation loss of 80 MW occurred due to loss of evacuation path at Tebhada Welspun S/S. 1. 220 kV Tebhada Welspun- Jamkhambalia 2. 220/33 kV Tebhada Welspun - ICT-1 3. 220/33 kV Tebhada Welspun - ICT-2 | grid_india_gd/grid_events/2026-09-01
G00505 | 2026-09 | 10 | GI-1 | Jammu and Kashmir | JK | Northern | 2026-09-20T17:41 | 2026-09-21T00:35 | 6.9 | 0 | 150 | FALSE | FALSE | FALSE | FALSE | FALSE | 10 GI-1 Jammu and Kashmir 20-09-2026 17:41 21-09-2026 00:35 06:54 0 150 0.00% 0.21% 53660 70683 i)220/132 kV Bishnah(JK) S/s has a double main bus scheme at the 220 kV level. ii)During the antecedent condition, as reported, 220/132 kV Bishnah(JK) S/s was operating in bus-split mode at both 220 kV an | 10 GI-1 Jammu and Kashmir 20-09-2026 17:41 21-09-2026 00:35 06:54 0 150 0.00% 0.21% 53660 70683 i)220/132 kV Bishnah(JK) S/s has a double main bus scheme at the 220 kV level. ii)During the antecedent condition, as reported, 220/132 kV Bishnah(JK) S/s was operating in bus-split mode at both 220 kV and 132 kV levels. 220 kV Samba(PG)–Bishnah(JK) (JK) Ckt and 220 kV Heera Nagar–Bishnah(JK) Ckt were feeding different loads under bus-split operation. 220 kV Samba(PG)–Bishnah(JK) (JK) Ckt. was carrying ~169 MW (as per SCADA). iii)As reported, at 17:41 hrs, the 220 kV Samba(PG)–Bishnah(JK) (JK) Ckt-1 tripped from Bishnah(JK) end due to burning of the R-phase CT dropper at the Bishnah(JK) end (detail of protection operated is yet to be shared). Due to the bus-split operation, tripping of the 220 kV Samba(PG)–Bishnah(JK) (JK) Ckt-1 resulted in load loss. iv)As per the PMU data at Samba(PG), no fault was observed. v)As per SCADA, a change in demand of ~150 MW was observed in the J&K Control Area. 1) 220 KV Samba(PG)-Bishnah(JK) (PDD JK) Ckt-1 | grid_india_gd/grid_events/2026-09-01
G00506 | 2026-09 | 46 | GI-1 | TELANGANA , ANDHRA PRADESH |  |  | 2026-09-20T22:39 | 2026-09-21T01:31 | 2.87 | 0 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | This led to the tripping of 220kV Bus-2 of Srisailam RB PH 220KV-DOMALAPENTA-SRISAILAM_RIGHT_BANK-1, 220KV- SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1, 220KV- SRISAILAM_RIGHT_BANK-MYDUKUR-1, 220KV- SRISAILAM_RIGHT_BANK-SOMAYAJULAPALLI-1 Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent | 19 GI-1 TELANGANA , ANDHRA PRADESH 20-09-2026 22:39 21-09-2026 01:31 02:52 0 0 0.00% 0.00% 47325.17 51592. 9 Tripping of 220kV Bus-2 of Srisailam RB PH of APGENCO As per the reports submitted, the triggering incident was R-G fault in 220kV Srisailam RB Markapuram line. At the same time 220kV Srisailam RB PH Bus-2 BBP maloperated due isolator status issue of 220kV Srisailam RB PH Markapuram line and all the lines connected to 220kV Srisailam RB PH Bus-2 tripped. This led to the tripping of 220kV Bus-2 of Srisailam RB PH 220KV-DOMALAPENTA-SRISAILAM_RIGHT_BANK-1, 220KV- SRISAILAM_RIGHT_BANK-NAGARJUNASAGAR_TS-1, 220KV- SRISAILAM_RIGHT_BANK-MYDUKUR-1, 220KV- SRISAILAM_RIGHT_BANK-SOMAYAJULAPALLI-1 Category of Grid Event ( GI 1 or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) | grid_india_gd/grid_events/2026-09-01
G00507 | 2026-09 | 34 | GD-1 | Maharashtra | MH | Western | 2026-09-21T17:08 | 2026-09-21T23:30 | 6.37 | 64 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, Tuljapur PSS-1 & 2 went dark and generation loss of 64 MW occurred. | 20 GD-1 Maharashtra 21-09-2026 17:08 21-09-2026 23:30 06:22 64 0 0.07% 0.0 0% 85724 69728 Complete outage of 220 kV Tuljapur sub station At 17:08 Hrs, 400kV- Tuljapur PSS 1- Konhali line tripped on Rph-Yph fault. Due to loss of evacuation path, Tuljapur PSS-1 & 2 went dark and generation loss of 64 MW occurred. 1. 400kV- Tuljapur PSS 1- Konhali line 2. 400kV- Tuljapur PSS 1- Tuljapur PSS 2 line 3. 400/33 kV Tuljapur PSS 1- ICT-1 4. 400/33 kV Tuljapur PSS 2- ICT-1 | grid_india_gd/grid_events/2026-09-01
G00508 | 2026-09 | 36 | GI-1 | DNHDD |  |  | 2026-09-22T10:51 | 2026-09-22T11:16 | 0.42 | 0 | 176 | FALSE | FALSE | FALSE | FALSE | FALSE | 22 GI-1 DNHDD 22-09-2026 10:51 22-09-2026 11:16 00:25 0 176 0.00% 0.26% 791 94 67876 Partial outage at 220 kV Magarwada sub station For loading of 220kV Daman-Magarwada Ckt#1 & 2, load change over from 220kV Bus-II to Bus-I at Magarwada S/s was under process. At 10:51 hrs, during closing of 220kV Bu | 22 GI-1 DNHDD 22-09-2026 10:51 22-09-2026 11:16 00:25 0 176 0.00% 0.26% 791 94 67876 Partial outage at 220 kV Magarwada sub station For loading of 220kV Daman-Magarwada Ckt#1 & 2, load change over from 220kV Bus-II to Bus-I at Magarwada S/s was under process. At 10:51 hrs, during closing of 220kV Bus Coupler R-phase pole of the 220 kV Bus Coupler not operated and an unbalanced three-phase system condition was created. Resulting in operation of the Earth Fault protection of the two incoming 220 kV Vapi–Magarwada lines and the three power transformers connected to Bus-II and Load loss of 176 MW occurred. However, 220kV Daman-Magarwada Ckt#1 & 2 and 220kV Bus#1 remained intact. 1. 220 kV Magarwada Bus coupler 2. 220 kV Magarwada Bus-2 3. 220 kV Magarwada-Vapi-1 4. 220 kV Magarwada-Vapi-2 5. 220/66 kV Magarwada ICT-4 6. 220/66 kV Magarwada ICT-2 7. 220/66 kV Magarwada ICT-3 | grid_india_gd/grid_events/2026-09-01
G00509 | 2026-09 | 14 | GD-1 | Haryana | HR | Northern | 2026-09-22T14:22 | 2026-09-22T16:05 | 1.72 | 0 | 511 | FALSE | FALSE | FALSE | FALSE | FALSE | 1) 220 KV Faridabad Sec-58 (HV)-Samaypur(BB) (HVPNL) Ckt-1 2) 220 KV Faridabad Sec-58 (HV)-Samaypur(BB) (PG) Ckt-2 3) 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 4) 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-2 5) 220/66 kV 100 MVA ICT-3 at Palli (HV) 6) 220/66 kV 160 MVA ICT-6 at Palli (HV) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) | 14 GD-1 Haryana 22-09-2026 14:22 22-09-2026 16:05 01:43 0 511 0.00% 0.62% 7 1620 82011 i)220KV Samaypur(BBMB) has double main bus scheme. There are four 220kV Buses i.e., Bus-1, Bus-2, Bus-3 and Bus-4. 400/220kV 500 MVA ICT-1,2,3&4 at Ballabhgarh(PG) feeds the 220kV Samaypur S/s. 220kV Faridabad GPS (NTPC) has double main and transfer bus scheme. Faridabad GPS (NTPC) is connected with 220kV Faridabad Sec-58 (HR) through double circuit and with 220kV Palla (HR) and 220kV Faridabad Sec-78 (HR) through single circuits. ii)During the antecedent condition, 220 KV Faridabad Sec-58 (HV)-Samaypur Ckt-1 & Ckt-2 were carrying ~170 MW each. All three units of Faridabad GPS (NTPC) were under outage. iii)As reported, at 14:22 hrs, 220 KV Faridabad Sec-58 (HV)-Samaypur(BB) (HVPNL) Ckt-1 was hand tripped due to heavy spaking in Y-phase wave trap. This led to overloading of 220 KV Faridabad Sec-58 (HV)-Samaypur(BB) (HVPNL) Ckt-2, which further tripped due to overloading. iv)As reported, at the same time, 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 & Ckt-2, 220/66 kV 100 MVA ICT-3 at Palli (HV), and 220/66 kV 160 MVA ICT-6 at Palli (HV) also tripped (exact nature of protection operated is yet to be share d. However, as per SCADA, power flow of 220 KV Samaypur(BB)-Palli(HV) (HVPNL) Ckt-1 & Ckt-2 was already zero at the time of event. v)As per PMU at Ballabhgarh(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 511 MW in Haryana control area was observed. 1) | grid_india_gd/grid_events/2026-09-01
G00510 | 2026-09 | 13 | GD-1 | Jammu and Kashmir | JK | Northern | 2026-09-22T16:06 | 2026-09-22T16:50 | 0.73 | 0 | 286 | FALSE | FALSE | FALSE | FALSE | FALSE | 13 GD-1 Jammu and Kashmir 22-09-2026 16:06 22-09-2026 16:50 00:44 0 286 0.00% 0.35% 66736 81876 i)220/132kV Barn(JK) is connected with 400/220kV Kishenpur(PG) through 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)During antecedent condition, all three 400/220kV 315 MVA ICTs were in serv | 13 GD-1 Jammu and Kashmir 22-09-2026 16:06 22-09-2026 16:50 00:44 0 286 0.00% 0.35% 66736 81876 i)220/132kV Barn(JK) is connected with 400/220kV Kishenpur(PG) through 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2. ii)During antecedent condition, all three 400/220kV 315 MVA ICTs were in service and were already operating above their rated capacity. ICT-1 & ICT-2 were carrying ~339 MVA each (~300 MW and ~157 MVAR) and was in increasing trend, and 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 were carrying ~170 MW each (as per SCADA). iii)As reported, at 16:06 hrs, 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 and Ckt-2 tripped due to operation of SPS at Kishenpur(PG). As per SPS logic at 400/220kV Kishenpur(PG), if loading of any 315MVA ICT at Kishenpur(PG) exceeds 110% of the rated capacity for 3 secs, 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) D/C shall trip. iv)As 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) D/C was the only 220kV source for 220/132kV Barn(JK) s/s, tripping of these circuits resulted in complete blackout of 220/132kV Barn(JK) s/s. v)As per PMU at Kishenpur(PG), no fault was observed in the system. vi)As per SCADA, change in demand of approx 286 MW was observed in J&K control area. 1) 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-1 2) 220 KV Kishenpur(PG)-Barn(JK) (PDD JK) Ckt-2 | grid_india_gd/grid_events/2026-09-01
G00511 | 2026-09 | 35 | GD-1 | Maharashtra | MH | Western | 2026-09-22T17:33 | 2026-09-22T19:13 | 1.67 | 44 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 44 MW occurred due to the event. | 21 GD-1 Maharashtra 22-09-2026 17:33 22-09-2026 19:13 01:40 44 0 0.06% 0.0 0% 76438 71007 Complete outage of 220 kV Jaulala sub station At 17:33 hrs, 220 kV Jaulala- Kallam S/C tripped on R-E fault. Due to loss of evacuation path, 220 kV Jaulala WPP went dark. Generation loss of 44 MW occurred due to the event. 1. 220 kV Jaulala- Kallam S/C | grid_india_gd/grid_events/2026-09-01
G00512 | 2026-09 | 12 | GD-1 | Haryana | HR | Northern | 2026-09-22T19:57 | 2026-09-22T21:34 | 1.62 | 226 | 1273 | FALSE | FALSE | FALSE | FALSE | FALSE | viii)As per SCADA, a change in demand of approx 1003 MW was observed in the Haryana control area and approx 270 MW in the Delhi control area; a generation loss of ~226 MW was observed at Faridabad GPS(NTPC) 1) 400/220 KV 500 MVA ICT 1 At Ballabhgarh(PG) 2) 400/220 KV 500 MVA ICT 2 At Ballabhgarh(PG) 3) 400/220 KV 500 MVA ICT 3 At Ballabhgarh(PG) 4) 220 KV Ballabhgarh-Samaypur (BB) Ckt-1 5) 220 KV | 12 GD-1 Haryana 22-09-2026 19:57 22-09-2026 21:34 01:37 226 1273 0.39% 1.6 0% 57794 79564 i)220kV Samaypur (BBMB) S/s has a four-buses with a bus sectionalizer between Bus-2 and Bus-3 and a bus coupler between Bus-3 and Bus-4; Bus-1 and Bus-4 are directly connected to each other through an isolator. There are twelve 220kV lines connected at 220kV Samaypur(BB): three circuits with 220kV Ballabhgarh(BB), two with 220kV Faridabad Sec-58 (HR), one with 220kV Charkhi Dadri (BB), two with 220kV Palli (HR), two with 220kV Badshahpur(HR), one with 220kV Palwal(HR), and one with 220kV Harfali(HR). Four 400/220kV 500 MVA ICTs at Ballabhgarh(PG) are the power source for 220kV Samaypur(BB). ii)Under the antecedent system conditions, all buses, the bus sectionalizer, the bus coupler, and all 220kV circuits, except 220kV FARIDABAD SEC-58 (HV)-SAMAYPUR(BB) (PG) CKT-1, were in service. The 400/220kV 500 MVA ICTs at Ballabhgarh(PG) were carrying ~200MW each. Faridabad GPS Units 1 & 2 (137.75 MW each) and Unit 3 (156.07 MW) were in service, generating ~226 MW. The generation of Faridabad GPS (NTPC) was being evacuated through 220 KV Faridabad Sec-58 (HV)-Faridabad(NT) Ckt-1 & Ckt-2 and the 220 KV Palla (HV)-Faridabad(NT) Ckt. iii)As reported by BBMB, at 19:57 hrs, a Y-phase-to-ground fault occurred due to a blast in the Y-phase CT of the bus coupler (connected between Bus-3 and Bus-4). Later, this Y-N fault converted into a 3-phase fault as the CTs of the other two phases also caught fire. Due | grid_india_gd/grid_events/2026-09-01
G00513 | 2026-09 | 50 | GD-1 | West Bengal | WB | Eastern | 2026-09-23T05:36 | 2026-09-23T07:00 | 1.4 | 528 | 252 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 528 MW and load loss of 252 MW reported at DPL S/s. | 4 GD-1 West Bengal 23-09-2026 05:36 23-09-2026 07:00 01:24 528 252 1.46% 1.01% 36113 25013 At 05:36 Hrs on 23.09.2026, B-phase CVT of Main Bus-2 at 220 kV switchyard got burst and bus fault occurred. All elements 220kV DPL - AB Zone D/C and 220kV DPL -Bidhannagar got tripped from remote end in Z-2 protection (Bus bar protection was not available at 220kV DPL S/s). DPL Unit-7 and Unit-8 tripped due to loss of evacuation path. Due to tripping of all elements from remote end, 220kV DPL S/s became dead. Generation loss of 528 MW and load loss of 252 MW reported at DPL S/s. 220kV-DPL- Bidhannagar 220kV-DPL-AB ZONE-1 220kV-DPL-AB ZONE-2 DPL Unit-7(300 MW) DPL Unit-8 (250 MW) | grid_india_gd/grid_events/2026-09-01
G00514 | 2026-09 | 37 | GD-1 | Gujarat | GJ | Western | 2026-09-24T16:34 | 2026-09-24T19:27 | 2.88 | 250 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 250 MW (139 MW & 111 MW) at 220 kV Vadva & 220 kV Devsar s/s respectively. | 23 GD-1 Gujarat 24-09-2026 16:34 24-09-2026 19:27 02:53 250 0 0.29% 0.00% 8 6388 70910 Complete outage at 220 kV Vadva and Devsar sub stations At 16:35 Hrs/ 24-09-2026, 220 kV Bhuj- Vadva line tripped on R-E fault. At the same time, 220 kV Bhuj- devsar line also tripped. Generation loss of 250 MW (139 MW & 111 MW) at 220 kV Vadva & 220 kV Devsar s/s respectively. 1. 220 kV Bhuj- Vadva 2. 220 kV Bhuj- devsar | grid_india_gd/grid_events/2026-09-01
G00515 | 2026-09 | 38 | GI-1 | Gujarat | GJ | Western | 2026-09-25T02:09 | 2026-09-25T03:00 | 0.85 | 0 | 730 | FALSE | FALSE | FALSE | FALSE | FALSE | 24 GI-1 Gujarat 25-09-2026 02:09 25-09-2026 03:00 00:51 0 730 0.00% 0.98% 7 4329 74199 Partial outage at 220 kV Sachin sub station Two separate events reported at 220/66kV Sachin GETCO SS. At 02:09Hrs, 220kV New Navsari-Sachin -2 line tripped due to conductor snapping. Line-1 also tripped due to car | 24 GI-1 Gujarat 25-09-2026 02:09 25-09-2026 03:00 00:51 0 730 0.00% 0.98% 7 4329 74199 Partial outage at 220 kV Sachin sub station Two separate events reported at 220/66kV Sachin GETCO SS. At 02:09Hrs, 220kV New Navsari-Sachin -2 line tripped due to conductor snapping. Line-1 also tripped due to carrier received at New Navsari end. As Bus coupler at Sachin SS was open, 220kV Bus#B along with connected 03 nos 220/66kV transformers tripped and load loss of 430MW occurred. While restoration of 66KV Sachin-Mangrol feeder, 66kV bus tripped at 03:11Hrs all elements connected to 66kV level tripped, resulting in load loss of 300MW. 1. 220kV Sachin-New Navsari Line-1 2. 220kV Sachin-New Navsari Line-2 3. 220kV Sachin Main Bus B 4. 220/66kV, 160MVA Sachin ICT-1 5. 220/66kV, 160MVA Sachin ICT-2 6. 220/66kV, 160MVA Sachin ICT-4 7. 220/66kV, 160MVA Sachin ICT-1 8. 220/66kV, 160MVA Sachin ICT-2 9. 220/66kV, 160MVA Sachin ICT-3 10.220/66kV, 160MVA Sachin ICT-4 11. 220/66kV, 160MVA Sachin ICT-5 | grid_india_gd/grid_events/2026-09-01
G00516 | 2026-09 | 51 | GD-1 | Jharkhand | JH | Eastern | 2026-09-25T12:13 | 2026-09-25T13:16 | 1.05 | 0 | 28 | FALSE | FALSE | FALSE | FALSE | FALSE | Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w. | 5 GD-1 Jharkhand 25-09-2026 12:13 25-09-2026 13:16 01:03 0 28 0.00% 0.13% 26594 20809 At 12:13 Hrs on 25/09/2026, R-Y fault occurred in line and both 220kV Daltonganj-Chatra and 220kV Latehar-Chatra line tripped from remote end in Z-3 protection, resulting in 220kV Chatra S/s became dead. Total load loss of 28 MW was reported at Chatra S/s. 220KV-DALTONGANJ-CHATRA-1220 kV Latehar–Chatra Elements Tripped Details of Grid Events during the Month of September 2026 in Eastern Region Sl No. Affected Area Time and Date of occurrence of Grid Event Time and Date of Restoration Duration(HH:MM) Loss of generation / loss of load during the Grid Event % Loss of generation / loss of load w.r.t Antecedent Generation/Load in the Regional Grid during the Grid Event Antecedent Generation/Load in the Regional Grid* Brief details of the event ( pre fault and post fault system conditions) Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD I Manipur 05-09-2026 13:32 05-09-2026 16:35 03:03 0 2 0.00% 0.07% 375 8 2941 Rengpang area of Manipur Power System was connected with rest of NER Grid through 132kV Loktak Rengpang line. The 132kV-Jiribam-Rengpang line was under long outage since 18:18 Hrs of 17.11.2023. At 13:32 Hrs of 05-09-2026, 132kV Loktak - Rengpang line tripped. Due to tripping of this element, Rengpang area of Manipur Power System was isolated from NER Grid and | grid_india_gd/grid_events/2026-09-01
G00517 | 2026-09 | 39 | GD-1 | Gujarat | GJ | Western | 2026-09-25T14:55 | 2026-09-25T16:26 | 1.52 | 1504 | 0 | FALSE | FALSE | FALSE | FALSE | TRUE | Due to loss of evacuation path, All RE generators connected to Khavda PS-III tripped and generation loss of 1504MW reported. | 25 GD-1 Gujarat 25-09-2026 14:55 25-09-2026 16:26 01:31 1504 0 2.01% 0.00% 74912 61847 Complete outage of 765/400 kV Khavda PS-3 (Powergrid WR-2) sub station At 14:55hrs, 765 kV Khavda PS-II Bus-3 tripped due to Busbar protection operation (suspected R-phase tracking problem in GIS). At the same time 765KV Khavda PS-II – Khavda PS-III ckt-1 tripped (from KPS-3 only). 765KV Khavda PS-II – Khavda PS-III- Ckt -2 was under planned outage along with A/R non-auto of ckt-1. Due to loss of evacuation path, All RE generators connected to Khavda PS-III tripped and generation loss of 1504MW reported. 765KV Khavda PS-II – Khavda PS-III ckt-1 synchronized at 16:26hrs. 1. 765 kV Khavda PS-2 – Khavda PS-3-1 2. 765/400 kV Khavda PS-3 ICT-1 3. 765/400 kV Khavda PS-3 ICT-2 4. 765/400 kV Khavda PS-3 ICT-3 5. 765/400 kV Khavda PS-3 ICT-4 6. 400 kV Khavda PSS8 – Khavda PS3 7. 400 kV Khavda PSS10 – Khavda PS3 8. 400 kV Khavda PSS11 – Khavda PS3 9. 400 kV Khavda PSS12 – Khavda PS3 10. 400 kV Khavda PSS13 – Khavda PS3 11. 400 kV Khavda PSS14 – Khavda PS3 12 .400 kV NTPC PSS-1 – Khavda PS3 13. 765 kV Khavda PS-II Bus 3 | grid_india_gd/grid_events/2026-09-01
G00518 | 2026-09 | 40 | GD-1 | Madhya Pradesh | MP | Western | 2026-09-26T09:56 | 2026-09-26T11:12 | 1.27 | 150 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 150 MW occurred at Shajapur U7 due loss of evacuation path and station became dark. | 26 GD-1 Madhya Pradesh 26-09-2026 09:56 26-09-2026 11:12 01:16 150 0 0.20% 0.00% 76412 63825 Complete outage of 220 kV Dehripal sub station At 10:53 Hrs/11-09-2026, 220kV Shajapur (Dehripal U7) -Pachora-1 S/C line tripped on over current protection operation. Generation loss of 150 MW occurred at Shajapur U7 due loss of evacuation path and station became dark. 1. 220kV Shajapur (Dehripal U7) -Pachora-1 S/C | grid_india_gd/grid_events/2026-09-01
G00519 | 2026-09 | 41 | GD-1 | Gujarat | GJ | Western | 2026-09-26T10:17 | 2026-10-01T01:11 | 110.9 | 6 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Due to loss of evacuation path, Juniper S/s became dead & Infirm Generation loss of around 6 MW occurred. | 27 GD-1 Gujarat 26-09-2026 10:17 01-10-2026 01:11 110:54 6 0 0.01% 0.00% 77 379 64805 Complete outage of 220 kV Juniper sub station At 10:17 Hrs/26-09-2026, 220KV Jamkhambaliya – Juniper Line tripped due to B-phase to Earth Fault. Due to loss of evacuation path, Juniper S/s became dead & Infirm Generation loss of around 6 MW occurred. 1. 220KV Jamkhambaliya – Juniper Line | grid_india_gd/grid_events/2026-09-01
G00520 | 2026-09 | 42 | GD-1 | Gujarat | GJ | Western | 2026-09-28T10:17 | 2026-09-30T17:35 | 55.3 | 57 | 0 | FALSE | FALSE | FALSE | FALSE | FALSE | Generation loss of 57 MW occurred due to loss of evacuation path. | 28 GD-1 Gujarat 28-09-2026 10:17 30-09-2026 17:35 55:18 57 0 0.07% 0.00% 78 390 67404 Complete outage of 400 kV Khavda PSS14 sub station At 06:59 Hrs, 400 kV Khavda PS 3-Khavda PSS-14 line tripped due to Yph-E fault. Indications at KPS3 end, Yph-E, z1, Fault distance-0.2 km, Fault current- 25 kA. Generation loss of 57 MW occurred due to loss of evacuation path. 400 kV Khavda PS 3-Khavda PSS-14 | grid_india_gd/grid_events/2026-09-01
G00521 | 2026-09 | 43 | GD-1 | Gujarat | GJ | Western | 2026-09-30T11:46 | 2026-09-30T13:44 | 1.97 | 0 | 440 | TRUE | TRUE | FALSE | FALSE | TRUE | 400/220KV Hazira ICT-1,2&3 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 ANDHRA PRADESH , ODISHA 05-09-2026 14:06 05-09-2026 15:34 01:28 0 0 0.00% 0.00% 57647.5 70291.3 Complete Outage of 220kV Upper Sileru PH of APGENCO During the antecedent conditions, all 220 | 29 GD-1 Gujarat 30-09-2026 11:46 30-09-2026 13:44 01:58 0 440 0.00% 0.59% 8 7055 73998 Complete outage of 400 kV Hazira (AMNSPTCL) sub station At 11:46Hrs, 400kV Gandhar Hazira line-1 tripped on Rph-E fault. As, 400kV Gandhar Hazira line-2 was under planned outage from 28-09.2026, AMNSIL station went dark and load loss of around 440MW occurred. By restoration of line-1 at 13:34Hrs, supply restored to 400kV AMNSIL S/S 1. 400KV Jhanor Hazira line-1 2. 400KV Hazira Bus-1&2 3. 400/220KV Hazira ICT-1,2&3 Category of Grid Event ( GI 1or GI 2/ GD-1 to GD-5) Generation Loss(MW) Load Loss (MW) % Generation Loss (MW) % Load Loss (MW) Antecedent Generation (MW) Antecedent Load (MW) 1 GD - 1 ANDHRA PRADESH , ODISHA 05-09-2026 14:06 05-09-2026 15:34 01:28 0 0 0.00% 0.00% 57647.5 70291.3 Complete Outage of 220kV Upper Sileru PH of APGENCO During the antecedent conditions, all 220 kV lines were connected to the 220 kV Upper Sileru Main Bus, while all units were connected to either the Main Bus or the Transfer Bus. The Transfer Bus was provided with a bus sectionalizer, as shown below. According to this configuration, if LBB operates due to the failure of any line breaker, all breakers will open, resulting in a complete outage of the station. As per the reports submitted, the triggering incident was a B-G fault on the 220 kV Upper Sileru-Balimela-1 line. At the Upper Sileru end, the fault was sensed in Zone 1; however, due to the B-phase pole of the line circuit breaker being stuck, the brea | grid_india_gd/grid_events/2026-09-01